## DCS TAG-PFI
SYSTEM | SUB-SYS | TAG LOCATION | EQUIPMENT | SENSOR | TAG SENSOR | Check | Unit | Threshold Status | S1L | S2L | S3L (Trip) | T1L | T2L | S1H (Alarm) | S2H (Fail) | T1H | T2H | NORMAL RANGE AT NEAR OR FULL LOAD | Check | Web_id |  | Id status
K3 & LH (KLH) | ABS | 3ABS-P888A | ABR RECIRC PUMP A | BRG TEMP 1 | 3ABS-TE866 | 1 |  | 1 | -999999 | -999999 |  | 0 | 0 | 100 | 105 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAOQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEEgTVRSIEJSRyBOTy4xIFRFTVA |  | 1
K3 & LH (KLH) | ABS | 3ABS-P888A | ABR RECIRC PUMP A | BRG TEMP 2 | 3ABS-TE867 | 1 |  | 1 | -999999 | -999999 |  | 0 | 0 | 75 | 105 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAOgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEEgTVRSIEJSRyBOTy4yIFRFTVA |  | 1
K3 & LH (KLH) | ABS | 3ABS-P888A | ABR RECIRC PUMP A | PRESSURE | 3ABS-PIX885 | 1 |  | 0 | -999999 |  |  | 0 |  | 3.75 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAPgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEEgT1VUTCBQUkVTUw |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | CURRENT | 3ABS-P888A-A | 1 |  | 0 | [6 empty] | 0-300A |  |  | Now:mati |  | F1DPw1kUu10ziUaXEx2rIyo4pATwAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFBIE1PVE9SIENVUlJFTlQ |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | BRG TEMP 1 | 3ABS-TE861 | 1 |  | 1 | -999999 | -999999 |  | 0 | 0 | 80 | 95 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAUAAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFBIE1PVE9SIElCIEJFQVJJTkc |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | BRG TEMP 2 | 3ABS-TE862 | 1 |  | 1 | -999999 | -999999 |  | 0 | 0 | 80 | 95 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAUQAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFBIE1PVE9SIE9CIEJFQVJJTkc |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | VIB MOTOR DE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAOQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEEgTVRSIEJSRyBOTy4xIFRFTVA |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | VIB MOTOR DE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAOQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEEgTVRSIEJSRyBOTy4xIFRFTVA |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | VIB MOTOR DE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAOQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEEgTVRSIEJSRyBOTy4xIFRFTVA |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | VIB MOTOR NDE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAOgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEEgTVRSIEJSRyBOTy4yIFRFTVA |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | VIB MOTOR NDE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAOgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEEgTVRSIEJSRyBOTy4yIFRFTVA |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | VIB MOTOR NDE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAOgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEEgTVRSIEJSRyBOTy4yIFRFTVA |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | STAT WDG TEMP U | 3ABS-TE863A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAUgAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFBIE1PVE9SIFNUQVRPUiBB |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | STAT WDG TEMP U | 3ABS-TE863B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAUwAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFBIE1PVE9SIFNUQVRPUiBC |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | STAT WDG TEMP V | 3ABS-TE864A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAVAAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFBIE1PVE9SIFNUQVRPUiBD |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | STAT WDG TEMP V | 3ABS-TE864B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAVQAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFBIE1PVE9SIFNUQVRPUiBE |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | STAT WDG TEMP W | 3ABS-TE865A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAVgAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFBIE1PVE9SIFNUQVRPUiBF |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888A | ABR RECIRC MOTOR PUMP A | STAT WDG TEMP W | 3ABS-TE865B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAVwAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFBIE1PVE9SIFNUQVRPUiBG |  | 1
K3 & LH (KLH) | ABS | 3ABS-P888B | ABR RECIRC PUMP B | BRG TEMP 1 | 3ABS-TE876 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAPwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEIgQlJHIE5PLjEgVEVNUA |  | 1
K3 & LH (KLH) | ABS | 3ABS-P888B | ABR RECIRC PUMP B | BRG TEMP 2 | 3ABS-TE877 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAQAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEIgQlJHIE5PLjIgVEVNUA |  | 1
K3 & LH (KLH) | ABS | 3ABS-P888B | ABR RECIRC PUMP B | PRESSURE | 3ABS-PIX886 | 1 |  |  | -999999 |  |  | 0 |  | 3.75 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pARwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEIgT1VUTCBQUkVTUw |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | CURRENT | 3ABS-P888B-A | 1 | [8 empty] | 0-300A |  |  | now:110 |  | F1DPw1kUu10ziUaXEx2rIyo4pAWgAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFCIE1PVE9SIENVUlJFTlQ |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | BRG TEMP 1 | 3ABS-TE871 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 80 | 95 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAWwAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFCIE1PVE9SIElCIEJFQVJJTkc |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | BRG TEMP 2 | 3ABS-TE872 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 80 | 95 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAXAAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFCIE1PVE9SIE9CIEJFQVJJTkc |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | VIB MOTOR DE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAQgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEIgTVRSIEJSRyBOTy4xIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | VIB MOTOR DE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAQgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEIgTVRSIEJSRyBOTy4xIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | VIB MOTOR DE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAQgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEIgTVRSIEJSRyBOTy4xIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | VIB MOTOR NDE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAQwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEIgTVRSIEJSRyBOTy4yIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | VIB MOTOR NDE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAQwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEIgTVRSIEJSRyBOTy4yIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | VIB MOTOR NDE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAQwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEIgTVRSIEJSRyBOTy4yIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | STAT WDG TEMP U | 3ABS-TE873A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAXQAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFCIE1PVE9SIFNUQVRPUiBB |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | STAT WDG TEMP U | 3ABS-TE873B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAXgAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFCIE1PVE9SIFNUQVRPUiBC |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | STAT WDG TEMP V | 3ABS-TE874A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAXwAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFCIE1PVE9SIFNUQVRPUiBD |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | STAT WDG TEMP V | 3ABS-TE874B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAYAAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFCIE1PVE9SIFNUQVRPUiBE |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | STAT WDG TEMP W | 3ABS-TE875A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAYQAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFCIE1PVE9SIFNUQVRPUiBF |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888B | ABR RECIRC MOTOR PUMP B | STAT WDG TEMP W | 3ABS-TE875B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAYgAAAAS1RKQi1LSTAwLVBJMVxUSkIxLkFCUyAxIFJFQ0lSQyBQVU1QIDFCIE1PVE9SIFNUQVRPUiBG |  | 1
K3 & LH (KLH) | ABS | 3ABS-P888C | ABR RECIRC PUMP C | BRG TEMP 1 | 3ABS-TE886 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 100 | 105 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pASAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgQlJHIE5PLjEgVEVNUA |  | 1
K3 & LH (KLH) | ABS | 3ABS-P888C | ABR RECIRC PUMP C | BRG TEMP 2 | 3ABS-TE887 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 75 | 105 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pASQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgQlJHIE5PLjIgVEVNUA |  | 1
K3 & LH (KLH) | ABS | 3ABS-P888C | ABR RECIRC PUMP C | PRESSURE | 3ABS-PIX887 | 1 |  |  | -999999 |  |  | 0 |  | 3.75 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAUAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgT1VUTCBQUkVTUw |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | CURRENT | 3ABS-P888C-A | 1 | [8 empty] | 0-300A |  |  | now:119 |  | F1DPw1kUu10ziUaXEx2rIyo4pASgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgQ1VS |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | BRG TEMP 1 | 3ABS-TE881 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 80 | 95 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pASwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIEJSRyBOTy4xIFRFTVA |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | BRG TEMP 2 | 3ABS-TE882 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 80 | 95 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pATAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIEJSRyBOTy4yIFRFTVA |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | VIB MOTOR DE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pASwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIEJSRyBOTy4xIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | VIB MOTOR DE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pASwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIEJSRyBOTy4xIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | VIB MOTOR DE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pASwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIEJSRyBOTy4xIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | VIB MOTOR NDE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pATAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIEJSRyBOTy4yIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | VIB MOTOR NDE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pATAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIEJSRyBOTy4yIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | VIB MOTOR NDE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pATAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIEJSRyBOTy4yIFRFTVA
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | STAT WDG TEMP U | 3ABS-TE883A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pATQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIFNUQVQgV0RHIFRFTVAgVQ |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | STAT WDG TEMP U | 3ABS-TE883B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pATQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIFNUQVQgV0RHIFRFTVAgVQ |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | STAT WDG TEMP V | 3ABS-TE884A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pATgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIFNUQVQgV0RHIFRFTVAgVg |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | STAT WDG TEMP V | 3ABS-TE884B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pATgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIFNUQVQgV0RHIFRFTVAgVg |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | STAT WDG TEMP W | 3ABS-TE885A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pATwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIFNUQVQgV0RHIFRFTVAgVw |  | 1
K3 & LH (KLH) | ABS | 3ABS-M888C | ABR RECIRC MOTOR PUMP C | STAT WDG TEMP W | 3ABS-TE885B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 120 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pATwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEMgTVRSIFNUQVQgV0RHIFRFTVAgVw |  | 1
K3 & LH (KLH) | ABS | 3ABS-M879A | ABR AGITATOR A MOTOR | CURRENT (A) | 3ABS-AG879A-A | 1 | [8 empty] | 100 |  |  | now: sekitar 60 |  | F1DPw1kUu10ziUaXEx2rIyo4pAHwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBBRyBBIENVUg |  | 1
K3 & LH (KLH) | ABS | 3ABS-M879B | ABR AGITATOR B MOTOR | CURRENT (A) | 3ABS-AG879B-A | 1 | [8 empty] | 100 |  |  | now: sekitar 61 |  | F1DPw1kUu10ziUaXEx2rIyo4pAIAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBBRyBCIENVUg |  | 1
K3 & LH (KLH) | ABS | 3ABS-M879C | ABR AGITATOR C MOTOR | CURRENT (A) | 3ABS-AG879C-A | 1 | [8 empty] | 100 |  |  | now: sekitar 62 |  | F1DPw1kUu10ziUaXEx2rIyo4pAIQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBBRyBDIENVUg |  | 1
K3 & LH (KLH) | ABS | 3ABS-M879D | ABR AGITATOR D MOTOR | CURRENT (A) | 3ABS-AG879D-A | 1 | [8 empty] | 100 |  |  | now: sekitar 63 |  | F1DPw1kUu10ziUaXEx2rIyo4pAIgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBBRyBEIENVUg |  | 1
K3 & LH (KLH) | ABS | 3ABS-M879E | ABR AGITATOR E MOTOR | CURRENT (A) | 3ABS-AG879E-A | 1 | [8 empty] | 100 |  |  | now: sekitar 64 |  | F1DPw1kUu10ziUaXEx2rIyo4pAIwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBBRyBFIENVUg |  | 1
SAC IAC (SAC) | ACR | 00ACR-C001A | AIR COMPRESSOR A MOTOR | AIR CP A MTR CUR | 00ACR-C001A-A | 1 | [8 empty] | 100 |  |  | now: sekitar 65 |  | F1DPw1kUu10ziUaXEx2rIyo4pAlgQAAAS1RKQi1LSTAwLVBJMVxUSkIxLlNFUlYgQUlSIENNUFIgQSBDVVJSRU5U
SAC IAC (SAC) | ACR | 00ACR-C001B | AIR COMPRESSOR B MOTOR | AIR CP B MTR CUR | 00ACR-C001B-A | 1 | [8 empty] | 100 |  |  | now: sekitar 66 |  | F1DPw1kUu10ziUaXEx2rIyo4pAlwQAAAS1RKQi1LSTAwLVBJMVxUSkIxLlNFUlYgQUlSIENNUFIgQiBDVVJSRU5U
SAC IAC (SAC) | ACR | 00ACR-C001C | AIR COMPRESSOR C MOTOR | AIR CP C MTR CUR | 00ACR-C001C-A | 1 | [8 empty] | 100 |  |  | now: sekitar 67 |  | F1DPw1kUu10ziUaXEx2rIyo4pAmAQAAAS1RKQi1LSTAwLVBJMVxUSkIxLlNFUlYgQUlSIENNUFIgQyBDVVJSRU5U
SAC IAC (SAC) | ACR | 00ACR-C001D | AIR COMPRESSOR D MOTOR | AIR CP D MTR CUR | 00ACR-C001D-A | [14 empty] | 0
Air Flue Gas (AFG) | AF | 3AF-F501A | FORCED DRAFT FAN A | BRG TEMP FREE SIDE (degC) | 3AF-TE521A | 1 | [7 empty] | 95 °C | Trip dengan expert judgement. S 95, Reset <93 |  |  | 40 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pApAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBBIEJSRyBURU1QIEZSRUUgU0lERQ |  | 1
Air Flue Gas (AFG) | AF | 3AF-F501A | FORCED DRAFT FAN A | BRG TEMP MOTOR SIDE (degC) | 3AF-TE522A | 1 | [7 empty] | 95 °C |  |  |  | 40 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pApQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBBIEJSRyBURU1QIE1PVE9SIFNJREU |  | 1
Air Flue Gas (AFG) | AF | 3AF-F501A | FORCED DRAFT FAN A | BRG VIB FREE SIDE (mm) | 3AF-VE501A | 1 | µm |  |  | 50µm |  | 0 |  | 130µm | Trip dengan expert judgement. S 130, Reset <125 | 0 |  | 50µm |  | F1DPw1kUu10ziUaXEx2rIyo4pApgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBBIEJSRyBWSUIgTU9OSVRPUiBGUkVFIFNJREU |  | 1
Air Flue Gas (AFG) | AF | 3AF-F501A | FORCED DRAFT FAN A | BRG VIB MOTOR SIDE (mm) | 3AF-VE502A | 1 |  |  |  | 50µm |  | 0 |  | 130µm |  | 0 |  | 50µm |  | F1DPw1kUu10ziUaXEx2rIyo4pApwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBBIEJSRyBWSUIgTU9OSVRPUiBNT1RPUiBTSURF |  | 1
Air Flue Gas (AFG) | AF | 3AF-F501A | FORCED DRAFT FAN A | BRG VIB MOTOR SIDE - HOR (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBVMQ
Air Flue Gas (AFG) | AF | 3AF-F501A | FORCED DRAFT FAN A | BRG VIB MOTOR SIDE - VER (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBWMQ
Air Flue Gas (AFG) | AF | 3AF-F501A | FORCED DRAFT FAN A | BRG VIB MOTOR SIDE - AXIAL (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAugwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBXMQ
Air Flue Gas (AFG) | AF | 3AF-F501A | FORCED DRAFT FAN A | BRG VIB FREE SIDE - HOR (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBVMg
Air Flue Gas (AFG) | AF | 3AF-F501A | FORCED DRAFT FAN A | BRG VIB FREE SIDE - VER (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBWMg
Air Flue Gas (AFG) | AF | 3AF-F501A | FORCED DRAFT FAN A | BRG VIB FREE SIDE - AXIAL (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBXMg
Air Flue Gas (AFG) | AF | 3AF-F501B | FORCED DRAFT FAN B | BRG TEMP FREE SIDE (degC) | 3AF-TE521B | 1 | [7 empty] | 95 °C |  |  |  | 40 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAqwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBCIEJSRyBURU1QIEZSRUUgU0lERQ |  | 1
Air Flue Gas (AFG) | AF | 3AF-F501B | FORCED DRAFT FAN B | BRG TEMP MOTOR SIDE (degC) | 3AF-TE522B | 1 | [7 empty] | 95 °C |  |  |  | 40 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pArAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBCIEJSRyBURU1QIE1PVE9SIFNJREU |  | 1
Air Flue Gas (AFG) | AF | 3AF-F501B | FORCED DRAFT FAN B | BRG VIB FREE SIDE (mm) | 3AF-VE501B | 1 | µm |  |  |  |  | 0 |  | 130µm |  | 0 |  | 50µm |  | F1DPw1kUu10ziUaXEx2rIyo4pArQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBCIEJSRyBWSUIgTU9OSVRPUiBGUkVFIFNJREU |  | 1
Air Flue Gas (AFG) | AF | 3AF-F501B | FORCED DRAFT FAN B | BRG VIB MOTOR SIDE (mm) | 3AF-VE502B | 1 | µm |  |  |  |  | 0 |  | 130µm |  | 0 |  | 50µm |  | F1DPw1kUu10ziUaXEx2rIyo4pArgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBCIEJSRyBWSUIgTU9OSVRPUiBNT1RPUiBTSURF |  | 1
Air Flue Gas (AFG) | AF | 3AF-F501B | FORCED DRAFT FAN B | BRG VIB MOTOR SIDE - HOR (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAvQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBVMQ
Air Flue Gas (AFG) | AF | 3AF-F501B | FORCED DRAFT FAN B | BRG VIB MOTOR SIDE - VER (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAvwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBWMQ
Air Flue Gas (AFG) | AF | 3AF-F501B | FORCED DRAFT FAN B | BRG VIB MOTOR SIDE - AXIAL (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBXMQ
Air Flue Gas (AFG) | AF | 3AF-F501B | FORCED DRAFT FAN B | BRG VIB FREE SIDE - HOR (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAvgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBVMg
Air Flue Gas (AFG) | AF | 3AF-F501B | FORCED DRAFT FAN B | BRG VIB FREE SIDE - VER (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBWMg
Air Flue Gas (AFG) | AF | 3AF-F501B | FORCED DRAFT FAN B | BRG VIB FREE SIDE - AXIAL (mm/s) | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBXMg
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | CURRENT (A) | 3AF-F501A-A | 1 |  |  | -999999 |  |  | 0 |  | 211 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAtQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1QgQ1VS |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | WDG TEMP U1 (degC) | 3AF-TE531A | 1 | [7 empty] | 150 °C | 160 °C (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAtgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBVMQ |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | WDG TEMP U2 (degC) | 3AF-TE532A | 1 | [7 empty] | 150 °C | 160 °C (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAtwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBVMg |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | WDG TEMP V1 (degC) | 3AF-TE533A | 1 | [7 empty] | 150 °C | 160 °C (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAuAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBWMQ |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | WDG TEMP V2 (degC) | 3AF-TE534A | 1 | [7 empty] | 150 °C | 160 °C (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAuQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBWMg |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | WDG TEMP W1 (degC) | 3AF-TE535A | 1 | [7 empty] | 150 °C | 160 °C (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAugwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBXMQ |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | WDG TEMP W2 (degC) | 3AF-TE536A | 1 | [7 empty] | 150 °C | 160 °C (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAuwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBXMg |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | WDG TEMP DE (degC) | 3AF-TE537A | 1 | [5 empty] | 0 |  | 95 °C | 100 °C | 0 |  | 45 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAqQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBBIE1PVE9SIEJSRyBURU1QIERF |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | WDG TEMP NDE (degC) | 3AF-TE538A | 1 | [5 empty] | 0 |  | 95 °C | 100 °C | 0 |  | 45 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAqgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBBIE1PVE9SIEJSRyBURU1QIE5ERQ |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | VIB MOTOR DE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBVMQ
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | VIB MOTOR DE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBWMQ
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | VIB MOTOR DE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAugwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBXMQ
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | VIB MOTOR NDE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBVMg
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | VIB MOTOR NDE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBWMg
Air Flue Gas (AFG) | AF | 3AF-M501A | FORCED DRAFT FAN A MOTOR | VIB MOTOR NDE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBXMg
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | CURRENT (A) | 3AF-F501B-A | 1 |  |  | -999999 |  |  | 0 |  | 211 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAvAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1QgQ1VS |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | WDG TEMP U1 (degC) | 3AF-TE531B | 1 | [7 empty] | 150 | 160 (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAvQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBVMQ |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | WDG TEMP U2 (degC) | 3AF-TE532B | 1 | [7 empty] | 150 | 160 (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAvgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBVMg |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | WDG TEMP V1 (degC) | 3AF-TE533B | 1 | [7 empty] | 150 | 160 (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAvwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBWMQ |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | WDG TEMP V2 (degC) | 3AF-TE534B | 1 | [7 empty] | 150 | 160 (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAwAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBWMg |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | WDG TEMP W1 (degC) | 3AF-TE535B | 1 | [7 empty] | 150 | 160 (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAwQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBXMQ |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | WDG TEMP W2 (degC) | 3AF-TE536B | 1 | [7 empty] | 150 | 160 (trip) |  |  | 60 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAwgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBXMg |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | WDG TEMP DE (degC) | 3AF-TE537B | 1 | [5 empty] | 0 |  | 95 °C | 100 °C | 0 |  | 45 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAsAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBCIE1PVE9SIEJSRyBURU1QIERF |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | WDG TEMP NDE (degC) | 3AF-TE538B | 1 | [5 empty] | 0 |  | 95 °C | 100ºC | 0 |  | 45 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAsQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZERiBCIE1PVE9SIEJSRyBURU1QIE5ERQ |  | 1
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | VIB MOTOR DE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAvQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBVMQ
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | VIB MOTOR DE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAvwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBWMQ
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | VIB MOTOR DE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBXMQ
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | VIB MOTOR NDE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAvgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBVMg
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | VIB MOTOR NDE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBWMg
Air Flue Gas (AFG) | AF | 3AF-M501B | FORCED DRAFT FAN B MOTOR | VIB MOTOR NDE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBXMg
Air Flue Gas (AFG) | AH | 3AH-AU501A | AH A SPEED REDUCER | AH A DIFF PRESS OF PRIMARY AIR SECONDARY AIR AND GAS SIDE | 3AH-DPI501A | [14 empty] | 0
Air Flue Gas (AFG) | AH | 3AH-AU501B | AH B SPEED REDUCER | AH B DIFF PRESS OF PRIMARY AIR SECONDARY AIR AND GAS SIDE | 3AH-DPI501B | [14 empty] | 0
Air Flue Gas (AFG) | AH | 3AH-H501A | REGENERATIVE AIR PREHEATER A
Air Flue Gas (AFG) | AH | 3AH-H501B | REGENERATIVE AIR PREHEATER B
Air Flue Gas (AFG) | AH | 3AH-M501A | REGENERATIVE AIR PREHEATER A MOTOR
Air Flue Gas (AFG) | AH | 3AH-M501B | REGENERATIVE AIR PREHEATER B MOTOR
Air Flue Gas (AFG) | AH | 3AH-M502A | RAPH A AIR MOTOR
Air Flue Gas (AFG) | AH | 3AH-M502B | RAPH B AIR MOTOR
Air Flue Gas (AFG) | AH | 3AH-M531A | RAPH A LUBRICATING OIL PUMP FOR HOT SIDE MOTOR
Air Flue Gas (AFG) | AH | 3AH-M531B | RAPH B LUBRICATING OIL PUMP FOR HOT SIDE MOTOR
Air Flue Gas (AFG) | AH | 3AH-P531A | RAPH A LUBRICATING OIL PUMP FOR HOT SIDE
Air Flue Gas (AFG) | AH | 3AH-P531B | RAPH B LUBRICATING OIL PUMP FOR HOT SIDE
Boiler (BOL) | AI | 3AI-M501A | WALL DESLAGGER A-1 MOTOR | WALL DESLAGGER A-1 | 3AI-Y501A | 1 | [11 empty] | Nilainya hanya Of dan On 0,1 |  | F1DPw1kUu10ziUaXEx2rIyo4pAbBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMQ |  | 1
Boiler (BOL) | AI | 3AI-M501B | WALL DESLAGGER B-1 MOTOR | WALL DESLAGGER B-1 | 3AI-Y501B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAbRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItMQ |  | 1
Boiler (BOL) | AI | 3AI-M501C | WALL DESLAGGER C-1 MOTOR | WALL DESLAGGER C-1 | 3AI-Y501C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAbhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMQ |  | 1
Boiler (BOL) | AI | 3AI-M501H | HALF RETRACTABLE SOOTBLOWER 17-R MOTOR | HALF RETRBL SB 17-R | 3AI-Y501H | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAvxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDE3LUw |  | 1
Boiler (BOL) | AI | 3AI-M501I | HALF RETRACTABLE SOOTBLOWER 17-L MOTOR | HALF RETRBL SB 17-L | 3AI-Y501I | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAvhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDE3LVI |  | 1
Boiler (BOL) | AI | 3AI-M501L | LONG RETRACTABLE SOOTBLOWER 1-L MOTOR | LONG RETRBL SB 1-L | 3AI-Y501L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAnhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDEtTA |  | 1
Boiler (BOL) | AI | 3AI-M501R | LONG RETRACTABLE SOOTBLOWER 1-R MOTOR | LONG RETRBL SB 1-R | 3AI-Y501R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAnxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDEtUg |  | 1
Boiler (BOL) | AI | 3AI-M502A | WALL DESLAGGER A-2 MOTOR | WALL DESLAGGER A-2 | 3AI-Y502A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAbxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMg |  | 1
Boiler (BOL) | AI | 3AI-M502B | WALL DESLAGGER B-2 MOTOR | WALL DESLAGGER B-2 | 3AI-Y502B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAcBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItMg |  | 1
Boiler (BOL) | AI | 3AI-M502C | WALL DESLAGGER C-2 MOTOR | WALL DESLAGGER C-2 | 3AI-Y502C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAcRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMg |  | 1
Boiler (BOL) | AI | 3AI-M502H | HALF RETRACTABLE SOOTBLOWER 18-R MOTOR | HALF RETRBL SB 18-R | 3AI-Y502H | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDE4LVI |  | 1
Boiler (BOL) | AI | 3AI-M502I | HALF RETRACTABLE SOOTBLOWER 18-L MOTOR | HALF RETRBL SB 18-L | 3AI-Y502I | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDE4LUw |  | 1
Boiler (BOL) | AI | 3AI-M502L | LONG RETRACTABLE SOOTBLOWER 2-L MOTOR | LONG RETRBL SB 2-L | 3AI-Y502L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAoRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDItTA |  | 1
Boiler (BOL) | AI | 3AI-M502R | LONG RETRACTABLE SOOTBLOWER 2-R MOTOR | LONG RETRBL SB 2-R | 3AI-Y502R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAoBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDItUg |  | 1
Boiler (BOL) | AI | 3AI-M503A | WALL DESLAGGER A-3 MOTOR | WALL DESLAGGER A-3 | 3AI-Y503A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAchcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMw |  | 1
Boiler (BOL) | AI | 3AI-M503B | WALL DESLAGGER B-3 MOTOR | WALL DESLAGGER B-3 | 3AI-Y503B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAcxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItMw |  | 1
Boiler (BOL) | AI | 3AI-M503C | WALL DESLAGGER C-3 MOTOR | WALL DESLAGGER C-3 | 3AI-Y503C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAdBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMw |  | 1
Boiler (BOL) | AI | 3AI-M503H | HALF RETRACTABLE SOOTBLOWER 19-R MOTOR | HALF RETRBL SB 19-R | 3AI-Y503H | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDE5LUw
Boiler (BOL) | AI | 3AI-M503I | HALF RETRACTABLE SOOTBLOWER 19-L MOTOR | HALF RETRBL SB 19-L | 3AI-Y503I | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDE5LVI
Boiler (BOL) | AI | 3AI-M503L | LONG RETRACTABLE SOOTBLOWER 3-L MOTOR | LONG RETRBL SB 3-L | 3AI-Y503L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAoxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDMtTA
Boiler (BOL) | AI | 3AI-M503R | LONG RETRACTABLE SOOTBLOWER 3-R MOTOR | LONG RETRBL SB 3-R | 3AI-Y503R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAohcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDMtUg
Boiler (BOL) | AI | 3AI-M504A | WALL DESLAGGER A-4 MOTOR | WALL DESLAGGER A-4 | 3AI-Y504A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAdRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtNA |  | 1
Boiler (BOL) | AI | 3AI-M504B | WALL DESLAGGER B-4 MOTOR | WALL DESLAGGER B-4 | 3AI-Y504B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAdhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItNA |  | 1
Boiler (BOL) | AI | 3AI-M504C | WALL DESLAGGER C-4 MOTOR | WALL DESLAGGER C-4 | 3AI-Y504C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAdxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtNA |  | 1
Boiler (BOL) | AI | 3AI-M504H | HALF RETRACTABLE SOOTBLOWER 20-R MOTOR | HALF RETRBL SB 20-R | 3AI-Y504H | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAxRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDIwLUw
Boiler (BOL) | AI | 3AI-M504I | HALF RETRACTABLE SOOTBLOWER 20-L MOTOR | HALF RETRBL SB 20-L | 3AI-Y504I | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAxBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDIwLVI
Boiler (BOL) | AI | 3AI-M504L | LONG RETRACTABLE SOOTBLOWER 4-L MOTOR | LONG RETRBL SB 4-L | 3AI-Y504L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pApRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDQtTA
Boiler (BOL) | AI | 3AI-M504R | LONG RETRACTABLE SOOTBLOWER 4-R MOTOR | LONG RETRBL SB 4-R | 3AI-Y504R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pApBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDQtUg
Boiler (BOL) | AI | 3AI-M505A | WALL DESLAGGER A-5 MOTOR | WALL DESLAGGER A-5 | 3AI-Y505A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAeBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtNQ
Boiler (BOL) | AI | 3AI-M505B | WALL DESLAGGER B-5 MOTOR | WALL DESLAGGER B-5 | 3AI-Y505B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAeRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItNQ
Boiler (BOL) | AI | 3AI-M505C | WALL DESLAGGER C-5 MOTOR | WALL DESLAGGER C-5 | 3AI-Y505C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAehcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtNQ
Boiler (BOL) | AI | 3AI-M505H | HALF RETRACTABLE SOOTBLOWER 21-R MOTOR | HALF RETRBL SB 21-R | 3AI-Y505H | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAxhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDIxLUw
Boiler (BOL) | AI | 3AI-M505I | HALF RETRACTABLE SOOTBLOWER 21-L MOTOR | HALF RETRBL SB 21-L | 3AI-Y505I | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAxxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDIxLVI
Boiler (BOL) | AI | 3AI-M505L | LONG RETRACTABLE SOOTBLOWER 5-L MOTOR | LONG RETRBL SB 5-L | 3AI-Y505L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pApxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDUtTA
Boiler (BOL) | AI | 3AI-M505R | LONG RETRACTABLE SOOTBLOWER 5-R MOTOR | LONG RETRBL SB 5-R | 3AI-Y505R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAphcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDUtUg
Boiler (BOL) | AI | 3AI-M506A | WALL DESLAGGER A-6 MOTOR | WALL DESLAGGER A-6 | 3AI-Y506A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAexcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtNg
Boiler (BOL) | AI | 3AI-M506B | WALL DESLAGGER B-6 MOTOR | WALL DESLAGGER B-6 | 3AI-Y506B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItNg
Boiler (BOL) | AI | 3AI-M506C | WALL DESLAGGER C-6 MOTOR | WALL DESLAGGER C-6 | 3AI-Y506C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtNg
Boiler (BOL) | AI | 3AI-M506H | HALF RETRACTABLE SOOTBLOWER 22-R MOTOR | HALF RETRBL SB 22-R | 3AI-Y506H | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAyRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDIyLUw
Boiler (BOL) | AI | 3AI-M506I | HALF RETRACTABLE SOOTBLOWER 22-L MOTOR | HALF RETRBL SB 22-L | 3AI-Y506I | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAyBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkhBTEYgUkVUUkJMIFNCIDIyLVI
Boiler (BOL) | AI | 3AI-M506L | LONG RETRACTABLE SOOTBLOWER 6-L MOTOR | LONG RETRBL SB 6-L | 3AI-Y506L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAqRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDYtTA
Boiler (BOL) | AI | 3AI-M506R | LONG RETRACTABLE SOOTBLOWER 6-R MOTOR | LONG RETRBL SB 6-R | 3AI-Y506R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAqBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDYtUg
Boiler (BOL) | AI | 3AI-M507A | WALL DESLAGGER A-7 MOTOR | WALL DESLAGGER A-7 | 3AI-Y507A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtNw
Boiler (BOL) | AI | 3AI-M507B | WALL DESLAGGER B-7 MOTOR | WALL DESLAGGER B-7 | 3AI-Y507B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItNw
Boiler (BOL) | AI | 3AI-M507C | WALL DESLAGGER C-7 MOTOR | WALL DESLAGGER C-7 | 3AI-Y507C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtNw
Boiler (BOL) | AI | 3AI-M507L | LONG RETRACTABLE SOOTBLOWER 7-L MOTOR | LONG RETRBL SB 7-L | 3AI-Y507L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAqxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDctTA
Boiler (BOL) | AI | 3AI-M507R | LONG RETRACTABLE SOOTBLOWER 7-R MOTOR | LONG RETRBL SB 7-R | 3AI-Y507R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAqhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDctUg
Boiler (BOL) | AI | 3AI-M508A | WALL DESLAGGER A-8 MOTOR | WALL DESLAGGER A-8 | 3AI-Y508A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtOA
Boiler (BOL) | AI | 3AI-M508B | WALL DESLAGGER B-8 MOTOR | WALL DESLAGGER B-8 | 3AI-Y508B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAghcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItOA
Boiler (BOL) | AI | 3AI-M508C | WALL DESLAGGER C-8 MOTOR | WALL DESLAGGER C-8 | 3AI-Y508C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtOA
Boiler (BOL) | AI | 3AI-M508L | LONG RETRACTABLE SOOTBLOWER 8-L MOTOR | LONG RETRBL SB 8-L | 3AI-Y508L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pArRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDgtTA
Boiler (BOL) | AI | 3AI-M508R | LONG RETRACTABLE SOOTBLOWER 8-R MOTOR | LONG RETRBL SB 8-R | 3AI-Y508R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pArBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDgtUg
Boiler (BOL) | AI | 3AI-M509A | WALL DESLAGGER A-9 MOTOR | WALL DESLAGGER A-9 | 3AI-Y509A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtOQ
Boiler (BOL) | AI | 3AI-M509B | WALL DESLAGGER B-9 MOTOR | WALL DESLAGGER B-9 | 3AI-Y509B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItOQ
Boiler (BOL) | AI | 3AI-M509C | WALL DESLAGGER C-9 MOTOR | WALL DESLAGGER C-9 | 3AI-Y509C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtOQ
Boiler (BOL) | AI | 3AI-M509L | LONG RETRACTABLE SOOTBLOWER 9-L MOTOR | LONG RETRBL SB 9-L | 3AI-Y509L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pArhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDktTA
Boiler (BOL) | AI | 3AI-M509R | LONG RETRACTABLE SOOTBLOWER 9-R MOTOR | LONG RETRBL SB 9-R | 3AI-Y509R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pArxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDktUg
Boiler (BOL) | AI | 3AI-M510A | WALL DESLAGGER A-10 MOTOR | WALL DESLAGGER A-10 | 3AI-Y510A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMTA
Boiler (BOL) | AI | 3AI-M510B | WALL DESLAGGER B-10 MOTOR | WALL DESLAGGER B-10 | 3AI-Y510B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAiBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItMTA
Boiler (BOL) | AI | 3AI-M510C | WALL DESLAGGER C-10 MOTOR | WALL DESLAGGER C-10 | 3AI-Y510C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAiRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMTA
Boiler (BOL) | AI | 3AI-M510L | LONG RETRACTABLE SOOTBLOWER 10-L MOTOR | LONG RETRBL SB 10-L | 3AI-Y510L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAsRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDEwLUw
Boiler (BOL) | AI | 3AI-M510R | LONG RETRACTABLE SOOTBLOWER 10-R MOTOR | LONG RETRBL SB 10-R | 3AI-Y510R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAsBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDEwLVI
Boiler (BOL) | AI | 3AI-M511A | WALL DESLAGGER A-11 MOTOR | WALL DESLAGGER A-11 | 3AI-Y511A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAihcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMTE
Boiler (BOL) | AI | 3AI-M511B | WALL DESLAGGER B-11 MOTOR | WALL DESLAGGER B-11 | 3AI-Y511B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAixcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItMTE
Boiler (BOL) | AI | 3AI-M511C | WALL DESLAGGER C-11 MOTOR | WALL DESLAGGER B-11 ABN | 3AI-Y511C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMTE
Boiler (BOL) | AI | 3AI-M511L | LONG RETRACTABLE SOOTBLOWER 11-L MOTOR | WALL DESLAGGER C-11 ABN | 3AI-Y511L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAshcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDExLUw
Boiler (BOL) | AI | 3AI-M511R | LONG RETRACTABLE SOOTBLOWER 11-R MOTOR | LONG RETRBL SB 11-R | 3AI-Y511R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAsxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDExLVI
Boiler (BOL) | AI | 3AI-M512A | WALL DESLAGGER A-12 MOTOR | WALL DESLAGGER A-12 | 3AI-Y512A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMTI
Boiler (BOL) | AI | 3AI-M512B | WALL DESLAGGER B-12 MOTOR | WALL DESLAGGER B-12 | 3AI-Y512B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItMTI
Boiler (BOL) | AI | 3AI-M512C | WALL DESLAGGER C-12 MOTOR | WALL DESLAGGER C-12 | 3AI-Y512C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMTI
Boiler (BOL) | AI | 3AI-M512L | LONG RETRACTABLE SOOTBLOWER 12-L MOTOR | LONG RETRBL SB 12-L | 3AI-Y512L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDEyLUw
Boiler (BOL) | AI | 3AI-M512R | LONG RETRACTABLE SOOTBLOWER 12-R MOTOR | LONG RETRBL SB 12-R | 3AI-Y512R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDEyLVI
Boiler (BOL) | AI | 3AI-M513A | WALL DESLAGGER A-13 MOTOR | WALL DESLAGGER A-13 | 3AI-Y513A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMTM
Boiler (BOL) | AI | 3AI-M513B | WALL DESLAGGER B-13 MOTOR | WALL DESLAGGER B-13 | 3AI-Y513B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItMTM
Boiler (BOL) | AI | 3AI-M513C | WALL DESLAGGER C-13 MOTOR | WALL DESLAGGER C-13 | 3AI-Y513C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMTM
Boiler (BOL) | AI | 3AI-M513L | LONG RETRACTABLE SOOTBLOWER 13-L MOTOR | LONG RETRBL SB 13-L | 3AI-Y513L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDEzLUw
Boiler (BOL) | AI | 3AI-M513R | LONG RETRACTABLE SOOTBLOWER 13-R MOTOR | LONG RETRBL SB 13-R | 3AI-Y513R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAthcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDEzLVI
Boiler (BOL) | AI | 3AI-M514A | WALL DESLAGGER A-14 MOTOR | WALL DESLAGGER A-14 | 3AI-Y514A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMTQ
Boiler (BOL) | AI | 3AI-M514B | WALL DESLAGGER B-14 MOTOR | WALL DESLAGGER B-14 | 3AI-Y514B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAlBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEItMTQ
Boiler (BOL) | AI | 3AI-M514C | WALL DESLAGGER C-14 MOTOR | WALL DESLAGGER C-14 | 3AI-Y514C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAlRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMTQ
Boiler (BOL) | AI | 3AI-M514L | LONG RETRACTABLE SOOTBLOWER 14-L MOTOR | LONG RETRBL SB 14-L | 3AI-Y514L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDE0LUw
Boiler (BOL) | AI | 3AI-M514R | LONG RETRACTABLE SOOTBLOWER 14-R MOTOR | LONG RETRBL SB 14-R | 3AI-Y514R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDE0LVI
Boiler (BOL) | AI | 3AI-M515A | WALL DESLAGGER A-15 MOTOR | WALL DESLAGGER A-15 | 3AI-Y515A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAlxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMTU
Boiler (BOL) | AI | 3AI-M515C | WALL DESLAGGER C-15 MOTOR | WALL DESLAGGER C-15 | 3AI-Y515C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAlhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMTU
Boiler (BOL) | AI | 3AI-M515L | LONG RETRACTABLE SOOTBLOWER 15-L MOTOR | LONG RETRBL SB 15-L | 3AI-Y515L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDE1LUw
Boiler (BOL) | AI | 3AI-M515R | LONG RETRACTABLE SOOTBLOWER 15-R MOTOR | LONG RETRBL SB 15-R | 3AI-Y515R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDE1LVI
Boiler (BOL) | AI | 3AI-M516A | WALL DESLAGGER A-16 MOTOR | WALL DESLAGGER A-16 | 3AI-Y516A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAmBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMTY
Boiler (BOL) | AI | 3AI-M516C | WALL DESLAGGER C-16 MOTOR | WALL DESLAGGER C-16 | 3AI-Y516C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAmRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMTY
Boiler (BOL) | AI | 3AI-M516L | LONG RETRACTABLE SOOTBLOWER 16-L MOTOR | LONG RETRBL SB 16-L | 3AI-Y516L | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAvRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDE2LUw
Boiler (BOL) | AI | 3AI-M516R | LONG RETRACTABLE SOOTBLOWER 16-R MOTOR | LONG RETRBL SB 16-R | 3AI-Y516R | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAvBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLkxPTkcgUkVUUkJMIFNCIDE2LVI
Boiler (BOL) | AI | 3AI-M517A | WALL DESLAGGER A-17 MOTOR | WALL DESLAGGER A-17 | 3AI-Y517A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAmhcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMTc
Boiler (BOL) | AI | 3AI-M517C | WALL DESLAGGER C-17 MOTOR | WALL DESLAGGER C-17 | 3AI-Y517C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAmxcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMTc
Boiler (BOL) | AI | 3AI-M518A | WALL DESLAGGER A-18 MOTOR | WALL DESLAGGER A-18 | 3AI-Y518A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAnBcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEEtMTg
Boiler (BOL) | AI | 3AI-M518C | WALL DESLAGGER C-18 MOTOR | WALL DESLAGGER C-18 | 3AI-Y518C | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAnRcAAAS1RKQi1LSTAwLVBJMVxUSkIzLldBTEwgREVTTEFHR0VSIEMtMTg
Boiler (BOL) | AI | 3AI-M551A | RAPH A SOOTBLOWER MOTOR | AH SOOTBLOWER A | 3AI-Y551A
Boiler (BOL) | AI | 3AI-M551B | RAPH B SOOTBLOWER MOTOR | AH SOOTBLOWER B | 3AI-Y551B
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG TEMP FREE SIDE | 3AL-TE521A | 1 |  |  |  | -999999 |  | 0 | 0 | 95 °C | 0-120degC | 0 | 0 | 50 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAdQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBBIEJSRyBURU1QIEZSRUUgU0lERQ |  | 1
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG TEMP MOTOR SIDE | 3AL-TE522A | 1 |  |  |  | -999999 |  | 0 | 0 | 95 °C | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAdg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBBIEJSRyBURU1QIE1PVE9SIFNJREU |  | 1
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(FREE SIDE) | 3AL-VE501A | 0 | µm |  | -999999 | -999999 |  | 0 | 0 | 75 um | 0-300um | 0 | 0 | now : 5,6um |  | F1DPw1kUu10ziUaXEx2rIyo4pAdw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBBIEJSRyBWSUIgTU9OSVRPUihGUkVFIFNJREUp |  | 1
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(FREE SIDE) - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVTE
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(FREE SIDE) - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVjE
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(FREE SIDE) - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAiQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVzE
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(MOTOR SIDE) | 3AL-VE502A | 0 |  |  | -999999 | -999999 |  | 0 | 0 | 75 um | 0-300um | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAeA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBBIEJSRyBWSUIgTU9OSVRPUihNT1RPUiBTSURFKQ |  | 1
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(MOTOR SIDE) - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVTI
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(MOTOR SIDE) - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAiA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVjI
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(MOTOR SIDE) - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAig4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVzI
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR (FREE SIDE MOTOR SIDE) | 3AL-VX501A, gak ketemu | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAdw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBBIEJSRyBWSUIgTU9OSVRPUihGUkVFIFNJREUp |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | CURRENT | 3AL-F501A-A | 1 | [8 empty] | 1000. Maksimum di OK sistem |  |  | now : 103 |  | F1DPw1kUu10ziUaXEx2rIyo4pAgg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1PVCBDVVI
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR WINDING TEMP-U1 | 3AL-TE531A | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAhQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVTE |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR WINDING TEMP-U2 | 3AL-TE532A | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAhg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVTI |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR WINDING TEMP-V1 | 3AL-TE533A | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAhw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVjE |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR WINDING TEMP-V2 | 3AL-TE534A | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAiA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVjI |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR WINDING TEMP-W1 | 3AL-TE535A | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAiQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVzE |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR WINDING TEMP-W2 | 3AL-TE536A | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAig4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1UUiBXSU5ESU5HIFRFTVAtVzI |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR BRG TEMP-DE | 3AL-TE537A | 1 | [5 empty] | 0 | 0 | 95 °C | 100 °C | 0 | 0 | 50 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAgw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1PVE9SIEJSRyBURU1QLURF |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR BRG TEMP-DE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1PVE9SIEJSRyBURU1QLURF
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR BRG TEMP-DE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1PVE9SIEJSRyBURU1QLURF
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR BRG TEMP-DE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1PVE9SIEJSRyBURU1QLURF
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR BRG TEMP-NDE | 3AL-TE538A | 1 | [5 empty] | 0 | 0 | 95 °C | 100 °C | 0 | 0 | 50 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAhA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1PVE9SIEJSRyBURU1QLU5ERQ |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR BRG TEMP-DE - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1PVE9SIEJSRyBURU1QLURF
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR BRG TEMP-DE - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1PVE9SIEJSRyBURU1QLURF
Air Flue Gas (AFG) | AL | 3AL-M501A | PRIMARY AIR FAN A MOTOR | MOTOR BRG TEMP-DE - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBBIE1PVE9SIEJSRyBURU1QLURF
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG TEMP FREE SIDE | 3AL-TE521B | 1 |  |  |  | -999999 |  | 0 | 0 | 95 °C | 999999 | 0 | 0 | 50 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAeg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBCIEJSRyBURU1QIEZSRUUgU0lERQ |  | 1
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG TEMP MOTOR SIDE | 3AL-TE522B | 1 |  |  |  | -999999 |  | 0 | 0 | 95 °C | 999999 | 0 | 0 | 50 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAew4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBCIEJSRyBURU1QIE1PVE9SIFNJREU |  | 1
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(FREE SIDE) | 3AL-VE501B | 0 | µm |  | -999999 | -999999 |  | 0 | 0 | 75 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBCIEJSRyBWSUIgTU9OSVRPUihGUkVFIFNJREUp |  | 1
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(FREE SIDE) - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVTE
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(FREE SIDE) - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVjE
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(FREE SIDE) - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVzE
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(MOTOR SIDE) | 3AL-VE502B | 0 |  |  | -999999 | -999999 |  | 0 | 0 | 75 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBCIEJSRyBWSUIgTU9OSVRPUihNT1RPUiBTSURFKQ |  | 1
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(MOTOR SIDE) - HOR | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVTI
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(MOTOR SIDE) - VER | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVjI
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(MOTOR SIDE) - AXIAL | NON DCS | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVzI
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB. MONITOR (FREE SIDE MOTOR SIDE) | 3AL-VX501B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBCIEJSRyBWSUIgTU9OSVRPUihGUkVFIFNJREUp |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501B | PRIMARY AIR FAN B MOTOR | CURRENT | 3AL-F501B-A, gak ketemu | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAiw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1PVCBDVVI
Air Flue Gas (AFG) | AL | 3AL-M501B | PRIMARY AIR FAN B MOTOR | MOTOR WINDING TEMP-U1 | 3AL-TE531B | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAjg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVTE |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501B | PRIMARY AIR FAN B MOTOR | MOTOR WINDING TEMP-U2 | 3AL-TE532B | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAjw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVTI |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501B | PRIMARY AIR FAN B MOTOR | MOTOR WINDING TEMP-V1 | 3AL-TE533B | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAkA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVjE |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501B | PRIMARY AIR FAN B MOTOR | MOTOR WINDING TEMP-V2 | 3AL-TE534B | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAkQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVjI |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501B | PRIMARY AIR FAN B MOTOR | MOTOR WINDING TEMP-W1 | 3AL-TE535B | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAkg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVzE |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501B | PRIMARY AIR FAN B MOTOR | MOTOR WINDING TEMP-W2 | 3AL-TE536B | 1 | [5 empty] | 0 | 0 | 150 °C | 160 °C (trip) | 0 | 0 | 65 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAkw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1UUiBXSU5ESU5HIFRFTVAtVzI |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501B | PRIMARY AIR FAN B MOTOR | MOTOR BRG TEMP-DE | 3AL-TE537B | 1 | [5 empty] | 0 | 0 | 95 °C | 100 °C | 0 | 0 | 50 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAjA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1PVE9SIEJSRyBURU1QLURF |  | 1
Air Flue Gas (AFG) | AL | 3AL-M501B | PRIMARY AIR FAN B MOTOR | MOTOR BRG TEMP-NDE | 3AL-TE538B | 1 | [5 empty] | 0 | 0 | 95 °C | 100 °C | 0 | 0 | 50 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAjQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBSSU1BUlkgQUlSIEZBTiBCIE1PVE9SIEJSRyBURU1QLU5ERQ |  | 1
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER A | PULVERIZER-A PRIMARY AIR FLOW (t/h) | 3AL-FX511A-N | [9 empty] | 150t/h |  |  | now: 100
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER A | PULVERIZER-A PRIMARY AIR FLOW (1) (mmH2O) | 3AL-FX511A-P | [9 empty] | 100mmH2O |  |  | now: 50an
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER A | PULVERIZER-A PRIMARY AIR FLOW (2) (mmH2O) | 3AL-FX512A-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER A | PULVERIZER-A PRIMARY AIR FLOW (3) (t/h) | 3AL-FX513A
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER A | PULVERIZER-A PRIMARY AIR FLOW (3) (mmH2O) | 3AL-FX513A-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER B | PULVERIZER-B PRIMARY AIR FLOW | 3AL-FX511B-N | [8 empty] | sama diatas
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER B | PULVERIZER-B PRIMARY AIR FLOW (1) | 3AL-FX511B-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER B | PULVERIZER-B PRIMARY AIR FLOW (2) (mmH2O) | 3AL-FX512B-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER B | PULVERIZER-B PRIMARY AIR FLOW (3) (t/h) | 3AL-FX513B
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER B | PULVERIZER-B PRIMARY AIR FLOW (3) (mmH2O) | 3AL-FX513B-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER C | PULVERIZER-C PRIMARY AIR FLOW | 3AL-FX511C-N | [8 empty] | Sama diatas
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER C | PULVERIZER-C PRIMARY AIR FLOW (1) | 3AL-FX511C-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER C | PULVERIZER-C PRIMARY AIR FLOW (2) (mmH2O) | 3AL-FX512C-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER C | PULVERIZER-C PRIMARY AIR FLOW (3) (t/h) | 3AL-FX513C
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER C | PULVERIZER-C PRIMARY AIR FLOW (3) (mmH2O) | 3AL-FX513C-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER D | PULVERIZER-D PRIMARY AIR FLOW | 3AL-FX511D-N | [8 empty] | sama diatas
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER D | PULVERIZER-D PRIMARY AIR FLOW (1) | 3AL-FX511D-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER D | PULVERIZER-D PRIMARY AIR FLOW (2) (mmH2O) | 3AL-FX512D-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER D | PULVERIZER-D PRIMARY AIR FLOW (3) (t/h) | 3AL-FX513D
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER D | PULVERIZER-D PRIMARY AIR FLOW (3) (mmH2O) | 3AL-FX513D-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER E | PULVERIZER-E PRIMARY AIR FLOW | 3AL-FX511E-N | [8 empty] | sama diatas
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER E | PULVERIZER-E PRIMARY AIR FLOW (1) | 3AL-FX511E-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER E | PULVERIZER-E PRIMARY AIR FLOW (2) (mmH2O) | 3AL-FX512E-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER E | PULVERIZER-E PRIMARY AIR FLOW (3) (t/h) | 3AL-FX513E
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER E | PULVERIZER-E PRIMARY AIR FLOW (3) (mmH2O) | 3AL-FX513E-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER F | PULVERIZER-F PRIMARY AIR FLOW | 3AL-FX511F-N | [8 empty] | sama diatas
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER F | PULVERIZER-F PRIMARY AIR FLOW (1) | 3AL-FX511F-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER F | PULVERIZER-F PRIMARY AIR FLOW (2) (mmH2O) | 3AL-FX512F-P
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER F | PULVERIZER-F PRIMARY AIR FLOW (3) (t/h) | 3AL-FX513F
Air Flue Gas (AFG) | AL | PART | PERFORMANCE - PULVERIZER F | PULVERIZER-F PRIMARY AIR FLOW (3) (mmH2O) | 3AL-FX513F-P
|  |  |  | PULV INLET PRIMARY HOT AIR PRESS | 3AL-PX510
|  |  |  | PULV INLET PRIMARY HOT AIR PRESS (1) | 3AL-PX510A | [9 empty] | -10 - 200mbarg
|  |  |  | PULV INLET PRIMARY HOT AIR PRESS (2) | 3AL-PX510B
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380/220V EMER D/P INCM CB CUR | CURRENT (A) | 00APC-CB851-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD MCC A INCM CB A CUR | CURRENT (A) | 00APC-CB852A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD MCC A INCM CB B CUR | CURRENT (A) | 00APC-CB852B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD MCC B INCM CB A CUR | CURRENT (A) | 00APC-CB853A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD MCC B INCM CB B CUR | CURRENT (A) | 00APC-CB853B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 10KV SB A 380V WWTPB A CB CUR | CURRENT (A) | 00APC-LV006A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V WWTPB A BUS V | VOLTAGE (V) | 00APC-LV006A-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 10KV SB B 380V WWTPB B CB CUR | CURRENT (A) | 00APC-LV006B-A
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V WWTPB B BUS V | VOLTAGE (V) | 00APC-LV006B-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V DEMIPB BUS V | VOLTAGE (V) | 00APC-MCC003-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGDWWTPB BUS V | VOLTAGE (V) | 00APC-MCC017-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380/220V FGD D/P BUS V | VOLTAGE (V) | 00APC-MCC851-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD MCC A BUS V | VOLTAGE (V) | 00APC-MCC852-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD BD A TO MCC A CB CUR | CURRENT (A) | 00APC-MCC852A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD BD B TO MCC A CB CUR | CURRENT (A) | 00APC-MCC852B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD MCC B BUS V | VOLTAGE (V) | 00APC-MCC853-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD BD A TO MCC B CB CUR | CURRENT (A) | 00APC-MCC853A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD BD B TO MCC B CB CUR | CURRENT (A) | 00APC-MCC853B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V/220V NLDP A BUS V | VOLTAGE (V) | 00APC-PD005A-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V/220V NLDP B BUS V | VOLTAGE (V) | 00APC-PD005B-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 10KV SB A 380V/220V WSB CB CUR | CURRENT (A) | 00APC-PD007-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V WSB BUS V | VOLTAGE (V) | 00APC-PD007-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V/220V ELDP BUS V | VOLTAGE (V) | 00APC-PD013-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD BD A INCM CUR | CURRENT (A) | 3APC-CB851A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V EMCC A INCM CB A CUR | CURRENT (A) | 3APC-CB852A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V EMCC A INCM CB B CUR | CURRENT (A) | 3APC-CB852B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD BD TIE CB CUR | CURRENT (A) | 3APC-CB853A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD BD A BUS V | VOLTAGE (V) | 3APC-LV851-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V UEB BUS V | VOLTAGE (V) | 3APC-MCC002-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD BD A TO EMCC A CB CUR | CURRENT (A) | 3APC-MCC851-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V EMCC A BUS V | VOLTAGE (V) | 3APC-MCC851-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD BD XFMR A CUR | CURRENT (A) | 3APC-TF851-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD BD XFMR A TEMP | TEMP (degC) | 3APC-TF851-T1 |  |  |  | -999999 |  |  | 0 |  | 120 |  | 0 |  |  |  | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V SSB A BUS V | VOLTAGE (V) | 00APC-LV001A-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V ESP BD A INCM CB CUR | CURRENT (A) | 3APC-CB810A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V ESP BD B INCM CB CUR | CURRENT (A) | 3APC-CB810B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V ESP BD TIE CB CUR | CURRENT (A) | 3APC-CB812A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 10KV UB A 380V TUB A CB CUR | CURRENT (A) | 3APC-LV001A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V TUB A BUS V | VOLTAGE (V) | 3APC-LV001A-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 10KV UB B 380V TUB B CB CUR | CURRENT (A) | 3APC-LV001B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V TUB B BUS V | VOLTAGE (V) | 3APC-LV001B-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 10KV UB A 380V BUB A CB CUR | CURRENT (A) | 3APC-LV501A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V BLR UNIT BD A BUS VOLT | VOLTAGE (V) | 3APC-LV501A-V | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 10KV UB B 380V BUB B CB CUR | CURRENT (A) | 3APC-LV501B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V BLR UNIT BD B BUS VOLT | VOLTAGE (V) | 3APC-LV501B-V | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 10KV UB A ESP UB A CB CUR | CURRENT (A) | 3APC-LV810A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V ESP BD A V | VOLTAGE (V) | 3APC-LV810A-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 10KV UB B ESP UB B CB CUR | CURRENT (A) | 3APC-LV810B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V ESP BD B V | VOLTAGE (V) | 3APC-LV810B-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 10KV UB A 380V FA BD A CB CUR | CURRENT (A) | 3APC-LV811-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V UEB BUS V | VOLTAGE (V) | 3APC-MCC002-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V FGD BD A TO EMCC A CB CUR | CURRENT (A) | 3APC-MCC851-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V EMCC A BUS V | VOLTAGE (V) | 3APC-MCC851-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APC | EQUIPMENT UNKNOWN | 380V SSB B BUS V | VOLTAGE (V) | 00APC-LV001B-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-MV001A | 10kV UNIT BOARD A | 10KV SB A BUS V | 00APE-MV001A-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-MV001B | 10kV UNIT BOARD B | 10KV SB B BUS V | 00APE-MV001B-V1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 00APE-MV801A | 10KV SB A 3KV TRIPPER BD A CB | 10KV SB A 3KV TRIPPER BD A CB CUR | 00APE-MV801A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 00APE-MV801B | 10KV SB B 3KV TRIPPER BD B CB | 10KV SB B 3KV TRIPPER BD B CB CUR | 00APE-MV801B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 00APE-MV802B | 10KV SB B 3KV CRSHR BD B CB | 10KV SB B 3KV CRSHR BD B CB CUR | 00APE-MV802B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 00APE-MV803B | 10KV SB B 3KV CL YD BD B CB | 10KV SB B 3KV CL YD BD B CB CUR | 00APE-MV803B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 00APE-MV807 | 10KV SB A 10KV CRSHR BD CB | 10KV SB A 10KV CRSHR BD CB CUR | 00APE-MV807-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB012A | 10KV UB A 10KV SB A BUS TIE CB-UNIT 3 | 10KV UB A 10KV SB A BUS TIE CB CUR U | 3APE-CB012A-A1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB012A | 10KV UB A 10KV SB A BUS TIE CB-UNIT 3 | 10KV UB A 10KV SB A BUS TIE CB CUR V | 3APE-CB012A-A2 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB012A | 10KV UB A 10KV SB A BUS TIE CB-UNIT 3 | 10KV UB A 10KV SB A BUS TIE CB CUR W | 3APE-CB012A-A3 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB012B | 10KV UB B 10KV SB B BUS TIE CB-UNIT 3 | 10KV UB B 10KV SB B BUS TIE CB CUR U | 3APE-CB012B-A1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB012B | 10KV UB B 10KV SB B BUS TIE CB-UNIT 3 | 10KV UB B 10KV SB B BUS TIE CB CUR V | 3APE-CB012B-A2 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB012B | 10KV UB B 10KV SB B BUS TIE CB-UNIT 3 | 10KV UB B 10KV SB B BUS TIE CB CUR W | 3APE-CB012B-A3 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB851A | 10KV FGD BD A INCM | PHAS L1 CUR | 3APE-CB851A-A1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB851A | 10KV FGD BD A INCM | PHAS L2 CUR | 3APE-CB851A-A2 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB851A | 10KV FGD BD A INCM | PHAS L3 CUR | 3APE-CB851A-A3 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB852A | 3KV FGD BD A INCM | PHAS L1 CUR | 3APE-CB852A-A1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB852A | 3KV FGD BD A INCM | PHAS L2 CUR | 3APE-CB852A-A2 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB852A | 3KV FGD BD A INCM | PHAS L3 CUR | 3APE-CB852A-A3 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB853A | 10KV FGD BD TIE CB | PHAS L1 CUR | 3APE-CB853A-A1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB853A | 10KV FGD BD TIE CB | PHAS L2 CUR | 3APE-CB853A-A2 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB853A | 10KV FGD BD TIE CB | PHAS L3 CUR | 3APE-CB853A-A3 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB854A | 3KV FGD BD TIE CB | PHAS L1 CUR | 3APE-CB854A-A1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB854A | 3KV FGD BD TIE CB | PHAS L2 CUR | 3APE-CB854A-A2 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB854A | 3KV FGD BD TIE CB | PHAS L3 CUR | 3APE-CB854A-A3 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-MV851 | 10KV UB B 10KV FGD BD A CB CUR | CURENT (A) | 3APE-MV851-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-MV852 | 10KV UB A 3KV FGD BD A CB CUR | CURENT (A) | 3APE-MV852-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB011A | 10KV UB INCM CB A | 10KV UB A INCM CB CUR U | 3APE-CB011A-A1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB011A | 10KV UB INCM CB A | 10KV UB A INCM CB CUR V | 3APE-CB011A-A2 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB011A | 10KV UB INCM CB A | 10KV UB A INCM CB CUR W | 3APE-CB011A-A3 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB011B | 10KV UB INCM CB B | 10KV UB B INCM CB CUR U | 3APE-CB011B-A1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB011B | 10KV UB INCM CB B | 10KV UB B INCM CB CUR V | 3APE-CB011B-A2 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB011B | 10KV UB INCM CB B | 10KV UB B INCM CB CUR W | 3APE-CB011B-A3 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB021A | 3KV UB INCM CB A | 3KV UB A INCM CB CUR U | 3APE-CB021A-A1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB021A | 3KV UB INCM CB A | 3KV UB A INCM CB CUR V | 3APE-CB021A-A2 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB021A | 3KV UB INCM CB A | 3KV UB A INCM CB CUR W | 3APE-CB021A-A3 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB021B | 3KV UB INCM CB B | 3KV UB B INCM CB CUR U | 3APE-CB021B-A1 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB021B | 3KV UB INCM CB B | 3KV UB B INCM CB CUR V | 3APE-CB021B-A2 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB021B | 3KV UB INCM CB B | 3KV UB B INCM CB CUR W | 3APE-CB021B-A3 | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-CB022A | 3KV UB BUS SECT BRKR CUR | CURRENT(A) | 3APE-CB022A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-MV002A | 10KV UB 3KV UB A CB A | CURRENT(A) | 3APE-MV002A-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-MV002B | 10KV UB 3KV UB A CB B | CURRENT(A) | 3APE-MV002B-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-MV851 | 10KV UB B 10KV FGD BD A CB CUR | CURRENT(A) | 3APE-MV851-A | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | APE | 3APE-MV852 | 10KV UB A 3KV FGD BD A CB CUR | CURRENT(A) | 3APE-MV852-A | [14 empty] | 0
Turbine (TUR) | AS | 3AS-BS010 | SILENCER FOR STEAM TURBINE | AUX STM HDR INL FLW | 3AS-FIX001 | 1 | mbar | [7 empty] | 0-120t/h |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAqQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFVWCBTVE0gSERSIElOTCBGTFc |  | 1
Turbine (TUR) | AS | 3AS-BS011 | SILENCER FOR STEAM TURBINE | AUX STM HDR PRESS | 3AS-PIX001 | 1 | [8 empty] | 0-25barg |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAqgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFVWCBTVE0gSERSIFBSRVNT |  | 1
Turbine (TUR) | AS | 3AS-BS012 | SILENCER FOR STEAM TURBINE | AUX ST PRESS CV (3RY SH HD) OUT PRESS | 3AS-PIX501 | 1 | [8 empty] | 0-25barg |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAoQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFVWCBTVCBQUkVTUyBDViAoM1JZIFNIIEhEKSBPVVQgUFJFU1M |  | 1
Turbine (TUR) | AS | 3AS-BS013 | SILENCER FOR STEAM TURBINE | AUX STM DRN SEP LVL (mm) | 3AS-LIX001 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 250 | 500 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pApQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFVWCBTVE0gRFJOIFNFUCBMVkw |  | 1
Turbine (TUR) | AS | 3AS-T010 | AUXILIARY STEAM DRAIN SEPARATOR | AUX STM HDR TEMP | 3AS-TE001 | 1 | [8 empty] | 0-500degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAqwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFVWCBTVE0gSERSIFRFTVA
Turbine (TUR) | AS | 3AS-T011 | AUXILIARY STEAM DRAIN SEPARATOR | AUX ST PRESS CV (3RY SH HD) OUT TEMP | 3AS-TE501 | 1 |  |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAogoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFVWCBTVCBQUkVTUyBDViAoM1JZIFNIIEhEKSBPVVQgVEVNUA
Turbine (TUR) | AS | 3AS-T012 | AUXILIARY STEAM DRAIN SEPARATOR | AUX STM HDR PRESS | 3AS-PIX001 | 1 | [8 empty] | 0-25barg |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAqgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFVWCBTVE0gSERSIFBSRVNT
Turbine (TUR) | AS | 3AS-T013 | AUXILIARY STEAM DRAIN SEPARATOR | AUX STM DRN SEP OUTL TEMP A | 3AS-TE002A | 1 | [8 empty] | 0-400degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pApgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFVWCBTVE0gRFJOIFNFUCBPVVRMIFRFTVAgQQ
Turbine (TUR) | AS | 3AS-T014 | AUXILIARY STEAM DRAIN SEPARATOR | AUX STM DRN SEP OUTL TEMP B | 3AS-TE002B | 1 | [8 empty] | 0-400degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pApwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFVWCBTVE0gRFJOIFNFUCBPVVRMIFRFTVAgQg
Ash Handling (ASH) | BAD | 3BAD-M501 | DRAG CHAIN CONVEYOR MOTOR
Ash Handling (ASH) | BAD | 3BAD-M511A | DCC COOLING WATER RECIRCULATION PUMP A MOTOR |  |  | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pARgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkRDQyBDT09MSU5HIFdBVEVSIFBI
Ash Handling (ASH) | BAD | 3BAD-M511B | DCC COOLING WATER RECIRCULATION PUMP B MOTOR |  |  | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pARgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkRDQyBDT09MSU5HIFdBVEVSIFBI
Ash Handling (ASH) | BAD | 3BAD-M521A | DCC SLUDGE PUMP A MOTOR | ON/OFF
Ash Handling (ASH) | BAD | 3BAD-M521B | DCC SLUDGE PUMP B MOTOR | ON/OFF
Ash Handling (ASH) | BAD | 3BAD-M531 | DCC CAUSTIC SODA TANK AGITATOR MOTOR | DCC MOTOR CURRENT | 3BAD-HSIG004 | 1 |  |  | -999999 |  |  |  |  | 10 | 17 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pARwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkRDQyBNT1RPUiBDVVJSRU5U
Ash Handling (ASH) | BAD | 3BAD-P511A | DCC COOLING WATER RECIRCULATION PUMP A | PUMP A BRG. TEMP. | 3BAD-TG510A | 1 | [8 empty] | harus lokal |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pANgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEEgQlJHIE5PLjEgVEVNUA
Ash Handling (ASH) | BAD | 3BAD-P511B | DCC COOLING WATER RECIRCULATION PUMP B | PUMP B BRG. TEMP. | 3BAD-TG510B | 1 | [8 empty] | haruslokal |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAQgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFCUiBSRUNJUkMgUE1QIEIgTVRSIEJSRyBOTy4xIFRFTVA
Ash Handling (ASH) | BAD | 3BAD-P521A | DCC SLUDGE PUMP A | ON/OFF
Ash Handling (ASH) | BAD | 3BAD-P521B | DCC SLUDGE PUMP B | ON/OFF
Ash Handling (ASH) | BAD | 3BAD-AG531 | DCC CAUSTIC SODA TANK AGITATOR | DCC COOLING WATER PH | 3BAD-AX501 | 1 |  |  | 2025-05-06 | 2025-05-06 |  |  |  |  | 2-13pH |  |  | 2025-09-07 |  | F1DPw1kUu10ziUaXEx2rIyo4pARgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkRDQyBDT09MSU5HIFdBVEVSIFBI
Ash Handling (ASH) | BAD | 3BAD-CV501 | DRAG CHAIN CONVEYOR |  | 3BAD-FE501
Ash Handling (ASH) | BAD | 3BAD-CR541 | CLINKER CRUSHER | DCC RECIRCULATION WATER FLOW | 3BAD-FX501 | 1 | t/h | [7 empty] | 0-55t/h |  |  | 40t/h |  | F1DPw1kUu10ziUaXEx2rIyo4pASAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkRDQyBSRUNJUkNVTEFUSU9OIFdBVEVSIEZMT1c
Ash Handling (ASH) | BAD | 3BAD-CR541 | CLINKER CRUSHER | DCC RECIRCULATION WATER FLOW | 3BAD-FX501-P | 1 | mbar | [7 empty] | 0-800mbar |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pASQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkRDQyBSRUNJUkNVTEFUSU9OIFdBVEVSIEZMT1cgLVA
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | BCP DIFF PRESS (barg) | 3BDW-DPIX501A-N | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAvwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUC1BIFNVQ1RJT04gRFJVTSBXQVRFUiBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | BCP DIFF PRESS (1) (barg) | 3BDW-DPIX501A | 1 |  |  | 1.049barg | 0.525barg | 0.208barg | 0 | 0 | 0.208barg | 999999 | 0 | 0 | 1.7barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAvwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUC1BIFNVQ1RJT04gRFJVTSBXQVRFUiBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | BCP DIFF PRESS (2) (barg) | 3BDW-DPIX502A | 1 |  |  | 1.049barg | 0.525barg | 0.208barg | 0 | 0 | 0.208barg | 999999 | 0 | 0 | 1.7barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAvwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUC1BIFNVQ1RJT04gRFJVTSBXQVRFUiBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | BCP DIFF PRESS (3) (barg) | 3BDW-DPIX503A | 1 |  |  | 1.049barg | 0.525barg | 0.208barg | 0 | 0 | 0.208barg | 999999 | 0 | 0 | 1.7barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAvwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUC1BIFNVQ1RJT04gRFJVTSBXQVRFUiBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | BCP A CASING TEMP | 3BDW-TE502A | 1 |  |  | -999999 |  |  | 0 | 0 | 349 | 999999 | 0 | 0 | 349 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAswoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBBIENBU0lORyBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | BCP CAVITY TEMP | 3BDW-TE503A | 1 | [7 empty] | 45 | 65 °C (trip) |  |  | 38 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAtAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBBIENBVklUWSBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | BCP A HEAT BARRIER COOLING WTR OUTL TEMP | 3CCCW-TX532A | 1 |  |  | -9999999 |  |  |  |  | 9999999 | 0-200degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAtQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBBIEhFQVQgQkFSUklFUiBDT09MSU5HIFdUUiBPVVRMIFRFTVA
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | BCP A MOTOR COOLER COOLING WTR TEMP | 3CCCW-TX531A | 1 | [7 empty] | 9999999 | 0-200degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAtgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBBIE1PVE9SIENPT0xFUiBDT09MSU5HIFdUUiBURU1Q
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | BRG VIB
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | BRG TEMP
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | FLOW RATE (t/h)
Boiler (BOL) | BDW | 3BDW-P521B | BOILER WATER CIRCULATION PUMP B | BCP DIFF PRESS (barg) | 3BDW-DPIX501B-N | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAxAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUC1CIFNVQ1RJT04gRFJVTSBXQVRFUiBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521B | BOILER WATER CIRCULATION PUMP B | BCP DIFF PRESS (1) (barg) | 3BDW-DPIX501B | 1 |  |  | 1.049barg | 0.525barg | 0.208barg | 0 | 0 | 0.208barg | 999999 | 0 | 0 | 1.7barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAxAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUC1CIFNVQ1RJT04gRFJVTSBXQVRFUiBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521B | BOILER WATER CIRCULATION PUMP B | BCP DIFF PRESS (2) (barg) | 3BDW-DPIX502B | 1 |  |  | 1.049barg | 0.525barg | 0.208barg | 0 | 0 | 0.208barg | 999999 | 0 | 0 | 1.7barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAxAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUC1CIFNVQ1RJT04gRFJVTSBXQVRFUiBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521B | BOILER WATER CIRCULATION PUMP B | BCP DIFF PRESS (3) (barg) | 3BDW-DPIX503B | 1 |  |  | 1.049barg | 0.525barg | 0.208barg | 0 | 0 | 0.208barg | 999999 | 0 | 0 | 1.7barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAxAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUC1CIFNVQ1RJT04gRFJVTSBXQVRFUiBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521B | BOILER WATER CIRCULATION PUMP B | BCP CASING TEMP | 3BDW-TE502B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 | 349 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAtwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBCIENBU0lORyBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521B | BOILER WATER CIRCULATION PUMP B | BCP CAVITY TEMP | 3BDW-TE503B | 1 | [7 empty] | 45 | 65 °C (trip) |  |  | 38 °C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAuAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBCIENBVklUWSBURU1Q |  | 1
Boiler (BOL) | BDW | 3BDW-P521B | BOILER WATER CIRCULATION PUMP B | BRG VIB
Boiler (BOL) | BDW | 3BDW-P521B | BOILER WATER CIRCULATION PUMP B | BRG TEMP
Boiler (BOL) | BDW | 3BDW-P521B | BOILER WATER CIRCULATION PUMP B | FLOW RATE (t/h)
Boiler (BOL) | BDW | 3BDW-T601 | STEAM DRUM | BCP-A SUCTION DRUM WATER TEMP | 3BDW-TE501A | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-500degC | 0 |  | 354 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAvwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUC1BIFNVQ1RJT04gRFJVTSBXQVRFUiBURU1Q
Boiler (BOL) | BDW | 3BDW-T601 | STEAM DRUM | BCP-B SUCTION DRUM WATER TEMP | 3BDW-TE501B | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-500degC | 0 |  | 354 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAxAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUC1CIFNVQ1RJT04gRFJVTSBXQVRFUiBURU1Q
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | DRUM PRESS (1) | 3BDW-PIX501 | 1 |  |  | 192.5barg |  |  | 0 |  | 999999 | 0-250barg | 0 |  | 182barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAaAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkRSVU0gUFJFU1MgKDEp |  | 1
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | DRUM PRESS | 3BDW-PIX501-N | 1 |  |  | -999999 | -999999 |  | 192.5 | 999999 | 0 | 0 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAZwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkRSVU0gUFJFU1M |  | 1
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | DRUM PRESS (2) | 3BDW-PIX502 | 1 |  |  | 192.5barg |  |  | 0 |  | 999999 | 0-250barg | 0 |  | 182barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAaQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkRSVU0gUFJFU1MgKDIp |  | 1
Boiler (BOL) | BDW | 3BDW-P521A | BOILER WATER CIRCULATION PUMP A | DRUM PRESS (3) | 3BDW-PIX503 | 1 |  |  | 192.5barg |  |  | 0 |  | 999999 | 0-250barg | 0 |  | 182barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAagwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkRSVU0gUFJFU1MgKDMp |  | 1
Boiler (BOL) | BDW | 3BDW-M521A | BOILER WATER CIRCULATION PUMP A MOTOR | CURRENT (A) | 3BDW-P521A-A | 1 |  |  | -999999 |  |  | 0 |  | 137 | 0-200-1000A | 0 |  | now:94 |  | F1DPw1kUu10ziUaXEx2rIyo4pAGgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJPSUxFUiBDSVJDVUxBVElPTiBQVU1QIEEgTU9UIENVUg |  | 1
Boiler (BOL) | BDW | 3BDW-M521A | BOILER WATER CIRCULATION PUMP A MOTOR | BRG TEMP
Boiler (BOL) | BDW | 3BDW-M521A | BOILER WATER CIRCULATION PUMP A MOTOR | BCP A CASING TEMP | 3BDW-TE502A | 1 | [8 empty] | 0-500degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAswoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBBIENBU0lORyBURU1Q
Boiler (BOL) | BDW | 3BDW-M521A | BOILER WATER CIRCULATION PUMP A MOTOR | STAT WDG TEMP
Boiler (BOL) | BDW | 3BDW-M521A | BOILER WATER CIRCULATION PUMP A MOTOR | BRG VIB
Boiler (BOL) | BDW | 3BDW-M521B | BOILER WATER CIRCULATION PUMP B MOTOR | CURRENT (A) | 3BDW-P521B-A | 1 |  |  | -999999 |  |  | 0 |  | 137 | 0-200-1000A | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAGwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJPSUxFUiBDSVJDVUxBVElPTiBQVU1QIEIgTU9UIENVUg |  | 1
Boiler (BOL) | BDW | 3BDW-M521B | BOILER WATER CIRCULATION PUMP B MOTOR | BRG TEMP
Boiler (BOL) | BDW | 3BDW-M521B | BOILER WATER CIRCULATION PUMP B MOTOR | BCP B CASING TEMP | 3BDW-TE502B | 1 | [8 empty] | 0-500degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAtwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBCIENBU0lORyBURU1Q
Boiler (BOL) | BDW | 3BDW-M521B | BOILER WATER CIRCULATION PUMP B MOTOR | STAT WDG TEMP
Boiler (BOL) | BDW | 3BDW-M521B | BOILER WATER CIRCULATION PUMP B MOTOR | BRG VIB
Boiler (BOL) | BFT | 3BFT-AU040A | BFPT A TURNING GEAR | BFPT STM HDR PRESS | 3BFT-PIX001 | 0 | [8 empty] | 1-15barg |  |  | now:6.67barg |  | F1DPw1kUu10ziUaXEx2rIyo4pABwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgU1RNIEhEUiBQUkVTUw
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT INL STM FLW | 3BFT-FIX001A | 1 | [8 empty] | 0-1280mbar |  |  | now:43.5 |  | F1DPw1kUu10ziUaXEx2rIyo4pA0goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBJTkwgU1RNIEZMVw |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT SPD (rpm) | 3BFT-SE001A-TR | 1 | [8 empty] | 0-7000 |  |  | 5161 |  | F1DPw1kUu10ziUaXEx2rIyo4pA2goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBTUEQgKFJQTSk |  | 1
Boiler (BOL) | BFT | 3BFT-AU040A | BFPT A TURNING GEAR | BFPT A SPD DMN FDBK | 3AEHC-CALC101 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA3AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBTUEQgRE1OIEZEQks
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT OVSP A | 3BFT-SE004A | 1 | RPM | [6 empty] | 7200(100%) | 8000(125%) |  |  | 5000an |  | F1DPw1kUu10ziUaXEx2rIyo4pA1woAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBPVlNQIEE |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT OVSP B | 3BFT-SE005A | 1 | [7 empty] | 7200(100%) | 8000 |  |  | 5000an |  | F1DPw1kUu10ziUaXEx2rIyo4pA2AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBPVlNQIEI |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT OVSP C | 3BFT-SE006A | 1 | RPM | [6 empty] | 7200(100%) | 8000 |  |  | 5000an |  | F1DPw1kUu10ziUaXEx2rIyo4pA2QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBPVlNQIEM |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT ZERO SPD | 3BFT-SE007A | 1 | [8 empty] | 0-7000 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA5goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBaRVJPIFNQRA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT EXH STM TEMP | 3BFT-TE001A | 1 |  |  | -999999 |  |  | 0 |  | 130 | 0-200degC | 0 |  | 42 |  | F1DPw1kUu10ziUaXEx2rIyo4pA0QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBFWEggU1RNIFRFTVA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT A CSG MET TEMP | 3BFT-TE002A | 1 | [8 empty] | 0-300degC |  |  | 273 |  | F1DPw1kUu10ziUaXEx2rIyo4pA0AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBDU0cgTUVUIFRFTVA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT THRST BRG FR/R MET TEMP | 3BFT-TE003A | 1 |  |  | -999999 |  |  | 0 |  | 93 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA3woAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBUSFJTVCBCUkcgRlIvUiBNRVQgVEVNUA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT THRST BRG FR/L MET TEMP | 3BFT-TE004A | 1 |  |  | -999999 |  |  | 0 |  | 93 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA3goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBUSFJTVCBCUkcgRlIvTCBNRVQgVEVNUA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT THRST BRG RR/R MET TEMP | 3BFT-TE005A | 1 |  |  | -999999 |  |  | 0 |  | 93 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA5QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBUSFJTVCBCUkcgUlIvUiBNRVQgVEVNUA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT THRST BRG RR/L MET TEMP | 3BFT-TE006A | 1 |  |  | -999999 |  |  | 0 |  | 93 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA5AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBUSFJTVCBCUkcgUlIvTCBNRVQgVEVNUA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT BRG 1 VIBN X | 3BFT-VE001A | 1 | µmpp |  | -999999 |  |  | 0 |  | 100 | 175umpp | 0 |  | 16 |  | F1DPw1kUu10ziUaXEx2rIyo4pAygoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBCUkcgMSBWSUJOIFg |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT BRG 1 VIBN Y | 3BFT-VE002A | 1 | µmpp |  | -999999 |  |  | 0 |  | 100 | 175umpp | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAywoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBCUkcgMSBWSUJOIFk |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT BRG 2 VIBN X | 3BFT-VE003A | 1 |  |  | -999999 |  |  | 0 |  | 100 | 175umpp | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAzQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBCUkcgMiBWSUJOIFg |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT BRG 2 VIBN Y | 3BFT-VE004A | 1 | µmpp |  | -999999 |  |  | 0 |  | 100 | 175umpp | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAzgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBCUkcgMiBWSUJOIFk |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT THRST BRG POSN A ABN | 3BFT-ZE001A-N | 1 |  |  | -0.4 |  | -0.7 | 0 |  | 0.68 | 0.98mm | 0 |  | 0-0.28 |  | F1DPw1kUu10ziUaXEx2rIyo4pA4QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBUSFJTVCBCUkcgUE9TTiBBIEFCTg |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT THRST BRG POSN B ABN | 3BFT-ZE002A-N | 1 | mm |  | -0.4 |  | -0.7 | 0 |  | 0.68 | 0.98mm | 0 |  | 0-0.28 |  | F1DPw1kUu10ziUaXEx2rIyo4pA4goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBUSFJTVCBCUkcgUE9TTiBCIEFCTg |  | 1
Boiler (BOL) | BFT | 3BFT-ST010A | BOILER FEEDWATER PUMP TURBINE A | BFPT THRST BRG POSN C ABN | 3BFT-ZE003A-N | 1 |  |  | -0.4 |  | -0.7 | 0 |  | 0.68 | 0.98mm | 0 |  | 0-0.28 |  | F1DPw1kUu10ziUaXEx2rIyo4pA4woAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBUSFJTVCBCUkcgUE9TTiBDIEFCTg |  | 1
Boiler (BOL) | BFT | 3BFT-AU040A | BFPT A TURNING GEAR | BFPT A CNTL OIL PRESS | 3EHT-PIX001A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAzwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBDTlRMIE9JTCBQUkVTUw
Boiler (BOL) | BFT | 3BFT-AU040A | BFPT A TURNING GEAR | BFPT A SSH PRESS | 3GST-PIX001A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA3QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBTU0ggUFJFU1M
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP | BFPT A LUB OIL FR DP | 3LOT-DPIX001A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA0woAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBMVUIgT0lMIEZSIERQ
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP | BFPT A LUB OIL PRESS | 3LOT-PIX001A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA1AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBMVUIgT0lMIFBSRVNT
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT INL STM FLW | 3BFT-FIX001B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA8AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBJTkwgU1RNIEZMVw |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT SPD (rpm) | 3BFT-SE001B-TR | 1 | RPM | [12 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA-AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBTUEQgKFJQTSk |  | 1
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP | BFPT B SPD DMN FDBK | 3BEHC-CALC101 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA-goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBTUEQgRE1OIEZEQks
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT OVSP A | 3BFT-SE004B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA9QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBPVlNQIEE |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT OVSP B | 3BFT-SE005B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA9goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBPVlNQIEI |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT OVSP C | 3BFT-SE006B | 1 | RPM | [12 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA9woAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBPVlNQIEM |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT ZERO SPD | 3BFT-SE007B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pABAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBaRVJPIFNQRA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT EXH STM TEMP | 3BFT-TE001B | 1 |  |  | -999999 |  |  | 0 |  | 130 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA7woAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBFWEggU1RNIFRFTVA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT A CSG MET TEMP | 3BFT-TE002B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA7goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBDU0cgTUVUIFRFTVA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT THRST BRG FR/R MET TEMP | 3BFT-TE003B | 1 |  |  | -999999 |  |  | 0 |  | 93 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA_QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBUSFJTVCBCUkcgRlIvUiBNRVQgVEVNUA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT THRST BRG FR/L MET TEMP | 3BFT-TE004B | 1 |  |  | -999999 |  |  | 0 |  | 93 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA_AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBUSFJTVCBCUkcgRlIvTCBNRVQgVEVNUA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT THRST BRG RR/R MET TEMP | 3BFT-TE005B | 1 |  |  | -999999 |  |  | 0 |  | 93 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAAwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBUSFJTVCBCUkcgUlIvUiBNRVQgVEVNUA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT THRST BRG RR/L MET TEMP | 3BFT-TE006B | 1 |  |  | -999999 |  |  | 0 |  | 93 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAAgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBUSFJTVCBCUkcgUlIvTCBNRVQgVEVNUA |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT BRG 1 VIBN X | 3BFT-VE001B | 1 | µmpp |  | -999999 |  |  | 0 |  | 100 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA6AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBCUkcgMSBWSUJOIFg |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT BRG 1 VIBN Y | 3BFT-VE002B | 1 | µmpp |  | -999999 |  |  | 0 |  | 100 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA6QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBCUkcgMSBWSUJOIFk |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT BRG 2 VIBN X | 3BFT-VE003B | 1 |  |  | -999999 |  |  | 0 |  | 100 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA6woAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBCUkcgMiBWSUJOIFg |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT BRG 2 VIBN Y | 3BFT-VE004B | 1 |  |  | -999999 |  |  | 0 |  | 100 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA7AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBCUkcgMiBWSUJOIFk |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT THRST BRG POSN A ABN | 3BFT-ZE001B-N | 1 | mm |  | -0.4 |  |  | 0 |  | 0.68 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA9QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBPVlNQIEE |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT THRST BRG POSN B ABN | 3BFT-ZE002B-N | 1 |  |  | -0.4 |  |  | 0 |  | 0.68 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA9goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBPVlNQIEI |  | 1
Boiler (BOL) | BFT | 3BFT-ST010B | BOILER FEEDWATER PUMP TURBINE B | BFPT THRST BRG POSN C ABN | 3BFT-ZE003B-N | 1 |  |  | -0.4 |  |  | 0 |  | 0.68 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA9woAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBPVlNQIEM |  | 1
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP | BFPT B CNTL OIL PRESS | 3EHT-PIX001B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA7QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBDTlRMIE9JTCBQUkVTUw
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP | BFPT B SSH PRESS | 3GST-PIX001B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA-woAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBTU0ggUFJFU1M
Feedwater (FW) | LOT | 3LOT-P080B | BFPT B OIL CONDITIONER FILTER PUMP | BFPT B LUB OIL FR DP | 3LOT-DPIX001B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA8QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBMVUIgT0lMIEZSIERQ
Feedwater (FW) | LOT | 3LOT-P080B | BFPT B OIL CONDITIONER FILTER PUMP | BFPT B LUB OIL PRESS | 3LOT-PIX001B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA8goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBMVUIgT0lMIFBSRVNT
Boiler (BOL) | BRS | 3BRS-H611 | PRIMARY REHEATER | 1RY RH OUTLET TEMP | 3BRS-TE501 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 384 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAogkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjFSWSBSSCBPVVRMRVQgVEVNUA |  | 1
Boiler (BOL) | BRS | 3BRS-H612 | PRIMARY REHEATER | 3RY RH OUTLET METAL TEMP (12P-NO1) | 3BRS-TE511 | 1 |  |  | 634 °C |  |  | 0 |  | 999999 | 0-700degC | 0 |  | 570 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA3wkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBSSCBPVVRMRVQgTUVUQUwgVEVNUCAoMTJQLU5PMSk |  | 1
Boiler (BOL) | BRS | 3BRS-H613 | PRIMARY REHEATER | 3RY RH OUTLET METAL TEMP (13P-NO1) | 3BRS-TE512 | 1 |  |  | 634 °C |  |  | 0 |  | 999999 | 0-700degC | 0 |  | 570 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA4AkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBSSCBPVVRMRVQgTUVUQUwgVEVNUCAoMTNQLU5PMSk |  | 1
Boiler (BOL) | BRS | 3BRS-H614 | PRIMARY REHEATER | 3RY RH OUTLET METAL TEMP (36P-NO1) | 3BRS-TE513 | 1 |  |  | 634 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 570 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA4QkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBSSCBPVVRMRVQgTUVUQUwgVEVNUCAoMzZQLU5PMSk |  | 1
Boiler (BOL) | BRS | 3BRS-H615 | PRIMARY REHEATER | 3RY RH OUTLET METAL TEMP (39P-NO1) | 3BRS-TE514 | 1 |  |  | 634 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 570 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA4gkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBSSCBPVVRMRVQgTUVUQUwgVEVNUCAoMzlQLU5PMSk |  | 1
Boiler (BOL) | BRS | 3BRS-H616 | PRIMARY REHEATER | 3RY RH OUTLET METAL TEMP (62P-NO1) | 3BRS-TE515 | 1 |  |  | 634 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 570 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA4wkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBSSCBPVVRMRVQgTUVUQUwgVEVNUCAoNjJQLU5PMSk |  | 1
Boiler (BOL) | BRS | 3BRS-H617 | PRIMARY REHEATER | 3RY RH OUTLET METAL TEMP (65P-NO1) | 3BRS-TE516 | 1 |  |  | 634 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 570 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA5AkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBSSCBPVVRMRVQgTUVUQUwgVEVNUCAoNjVQLU5PMSk |  | 1
Boiler (BOL) | BRS | 3BRS-H618 | PRIMARY REHEATER | 3RY RH OUTLET METAL TEMP (74P-NO1) | 3BRS-TE517 | 1 |  |  | 634 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 570 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA5QkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBSSCBPVVRMRVQgTUVUQUwgVEVNUCAoNzRQLU5PMSk |  | 1
Boiler (BOL) | BRS | 3BRS-H619 | PRIMARY REHEATER | 3RY RH OUTLET METAL TEMP (77P-NO1) | 3BRS-TE518 | 1 |  |  | 634 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 570 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA5gkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBSSCBPVVRMRVQgTUVUQUwgVEVNUCAoNzdQLU5PMSk |  | 1
Boiler (BOL) | BSS | 3BSS-H611 | PRIMARY SUPERHEATER | 1RY SH OUTLET DSH INLET STEAM A TEMP | 3BSS-TE501A | 1 | [5 empty] | 0 |  |  | 0-600degC | 0 |  | 419 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pApwkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjFSWSBTSCBPVVRMRVQgRFNILUEgSU5MRVQgU1RFQU0gVEVNUA
Boiler (BOL) | BSS | 3BSS-H612 | PRIMARY SUPERHEATER | 2RY SH INLET STEAM A TEMP (1) | 3BSS-TE502A | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 415 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAvAkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBJTkxFVCBTVEVBTSBBIFRFTVAgKDEp |  | 1
Boiler (BOL) | BSS | 3BSS-H613 | PRIMARY SUPERHEATER | 2RY SH INLET STEAM A TEMP | 3BSS-TE502A-DU | 1 | [8 empty] | 0-600degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAvAkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBJTkxFVCBTVEVBTSBBIFRFTVAgKDEp
Boiler (BOL) | BSS | 3BSS-H614 | PRIMARY SUPERHEATER | 2RY SH INLET STEAM A TEMP | 3BSS-TE502A-N | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAvQkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBJTkxFVCBTVEVBTSBBIFRFTVAgKDIp
Boiler (BOL) | BSS | 3BSS-H615 | PRIMARY SUPERHEATER | 2RY SH INLET STEAM A TEMP (2) | 3BSS-TE503A | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 415 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAvQkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBJTkxFVCBTVEVBTSBBIFRFTVAgKDIp |  | 1
Boiler (BOL) | BSS | 3BSS-H616 | PRIMARY SUPERHEATER | 2RY SH OUTLET STEAM A TEMP (1) | 3BSS-TE504A | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 464 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA2gkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgU1RFQU0gQSBURU1QICgxKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H617 | PRIMARY SUPERHEATER | 2RY SH OUTLET STEAM A TEMP | 3BSS-TE504A-DU | 1 | [8 empty] | 0-600degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA2gkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgU1RFQU0gQSBURU1QICgxKQ
Boiler (BOL) | BSS | 3BSS-H618 | PRIMARY SUPERHEATER | 2RY SH OUTLET STEAM A TEMP | 3BSS-TE504A-N | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA2wkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgU1RFQU0gQSBURU1QICgyKQ
Boiler (BOL) | BSS | 3BSS-H619 | PRIMARY SUPERHEATER | 2RY SH OUTLET STEAM A TEMP (2) | 3BSS-TE505A | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 464 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA2wkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgU1RFQU0gQSBURU1QICgyKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H620 | PRIMARY SUPERHEATER | 3RY SH INLET STEAM A TEMP (1) | 3BSS-TE506A | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 454 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA9gkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBJTkxFVCBTVEVBTSBBIFRFTVAgKDEp |  | 1
Boiler (BOL) | BSS | 3BSS-H621 | PRIMARY SUPERHEATER | 3RY SH INLET STEAM A TEMP | 3BSS-TE506A-DU | 1 | [8 empty] | 0-600degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA9gkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBJTkxFVCBTVEVBTSBBIFRFTVAgKDEp
Boiler (BOL) | BSS | 3BSS-H622 | PRIMARY SUPERHEATER | 3RY SH INLET STEAM A TEMP | 3BSS-TE506A-N | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA9wkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBJTkxFVCBTVEVBTSBBIFRFTVAgKDIp
Boiler (BOL) | BSS | 3BSS-H623 | PRIMARY SUPERHEATER | 3RY SH INLET STEAM A TEMP (2) | 3BSS-TE507A | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 454 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA9wkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBJTkxFVCBTVEVBTSBBIFRFTVAgKDIp |  | 1
Boiler (BOL) | BSS | 3BSS-H640 | PRIMARY SUPERHEATER | 1RY SH OUTLET DSH INLET STEAM B TEMP | 3BSS-TE501B | 1 | [5 empty] | 0 |  |  | 0-600degC | 0 |  | 419 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAqAkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjFSWSBTSCBPVVRMRVQgRFNILUIgSU5MRVQgU1RFQU0gVEVNUA
Boiler (BOL) | BSS | 3BSS-H641 | PRIMARY SUPERHEATER | 2RY SH INLET STEAM B TEMP (1) | 3BSS-TE502B | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 415 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAxAkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBJTkxFVCBTVEVBTSBCIFRFTVAgKDEp |  | 1
Boiler (BOL) | BSS | 3BSS-H642 | PRIMARY SUPERHEATER | 2RY SH INLET STEAM B TEMP | 3BSS-TE502B-DU | 1 | [8 empty] | 0-600degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAxAkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBJTkxFVCBTVEVBTSBCIFRFTVAgKDEp
Boiler (BOL) | BSS | 3BSS-H643 | PRIMARY SUPERHEATER | 2RY SH INLET STEAM B TEMP | 3BSS-TE502B-N | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAxQkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBJTkxFVCBTVEVBTSBCIFRFTVAgKDIp
Boiler (BOL) | BSS | 3BSS-H644 | PRIMARY SUPERHEATER | 2RY SH INLET STEAM B TEMP (2) | 3BSS-TE503B | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 415 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAxQkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBJTkxFVCBTVEVBTSBCIFRFTVAgKDIp |  | 1
Boiler (BOL) | BSS | 3BSS-H645 | PRIMARY SUPERHEATER | 2RY SH OUTLET STEAM B TEMP (1) | 3BSS-TE504B | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 464 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA3QkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgU1RFQU0gQiBURU1QICgxKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H646 | PRIMARY SUPERHEATER | 2RY SH OUTLET STEAM B TEMP | 3BSS-TE504B-DU | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA3QkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgU1RFQU0gQiBURU1QICgxKQ
Boiler (BOL) | BSS | 3BSS-H647 | PRIMARY SUPERHEATER | 2RY SH OUTLET STEAM B TEMP | 3BSS-TE504B-N | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA3gkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgU1RFQU0gQiBURU1QICgyKQ
Boiler (BOL) | BSS | 3BSS-H648 | PRIMARY SUPERHEATER | 2RY SH OUTLET STEAM B TEMP (2) | 3BSS-TE505B | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 464 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA3gkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgU1RFQU0gQiBURU1QICgyKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H649 | PRIMARY SUPERHEATER | 3RY SH INLET STEAM B TEMP (1) | 3BSS-TE506B | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-600degC | 0 |  | 454 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA9gkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBJTkxFVCBTVEVBTSBBIFRFTVAgKDEp |  | 1
Boiler (BOL) | BSS | 3BSS-H650 | PRIMARY SUPERHEATER | 3RY SH INLET STEAM B TEMP | 3BSS-TE506B-DU | 1 | [8 empty] | 0-600degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA_gkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBJTkxFVCBTVEVBTSBCIFRFTVAgKDEp
Boiler (BOL) | BSS | 3BSS-H651 | PRIMARY SUPERHEATER | 3RY SH INLET STEAM B TEMP | 3BSS-TE506B-N | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA_wkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBJTkxFVCBTVEVBTSBCIFRFTVAgKDIp
Boiler (BOL) | BSS | 3BSS-H652 | PRIMARY SUPERHEATER | 3RY SH INLET STEAM B TEMP (2) | 3BSS-TE507B | 1 |  |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  | 454 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA9wkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBJTkxFVCBTVEVBTSBBIFRFTVAgKDIp |  | 1
Boiler (BOL) | BSS | 3BSS-H624 | PRIMARY SUPERHEATER | 2RY SH OUTLET METAL TEMP (1P-NO2) | 3BSS-TE511 | 1 |  |  | 513 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 469 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA0wkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoMVAtTk8yKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H625 | PRIMARY SUPERHEATER | 2RY SH OUTLET METAL TEMP (2P-NO2) | 3BSS-TE512 | 1 |  |  | 513 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 469 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA1AkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoMlAtTk8yKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H626 | PRIMARY SUPERHEATER | 2RY SH OUTLET METAL TEMP (3P-NO2) | 3BSS-TE513 | 1 |  |  | 513 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 469 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA1QkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoM1AtTk8yKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H627 | PRIMARY SUPERHEATER | 2RY SH OUTLET METAL TEMP (4P-NO2) | 3BSS-TE514 | 1 |  |  | 513 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 469 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA1gkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoNFAtTk8yKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H628 | PRIMARY SUPERHEATER | 2RY SH OUTLET METAL TEMP (5P-NO2) | 3BSS-TE515 | 1 |  |  | 513 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 469 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA1wkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoNVAtTk8yKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H629 | PRIMARY SUPERHEATER | 2RY SH OUTLET METAL TEMP (6P-NO2) | 3BSS-TE516 | 1 |  |  | 513 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 469 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pA2AkAAAS1RKQi1LSTAwLVBJMVxUSkIzLjJSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoNlAtTk8yKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H630 | PRIMARY SUPERHEATER | 3RY SH OUTLET METAL TEMP (2P-NO2) | 3BSS-TE531 | 1 |  |  | 593 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 556 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAGQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoMlAtTk8yKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H631 | PRIMARY SUPERHEATER | 3RY SH OUTLET METAL TEMP (7P-NO2) | 3BSS-TE532 | 1 |  |  | 593 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 556 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAHAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoN1AtTk8yKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H632 | PRIMARY SUPERHEATER | 3RY SH OUTLET METAL TEMP (13P-NO2) | 3BSS-TE533 | 1 |  |  | 593 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 556 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAFgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoMTNQLU5PMik |  | 1
Boiler (BOL) | BSS | 3BSS-H633 | PRIMARY SUPERHEATER | 3RY SH OUTLET METAL TEMP (19P-NO2) | 3BSS-TE534 | 1 |  |  | 593 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 556 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAFwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoMTlQLU5PMik |  | 1
Boiler (BOL) | BSS | 3BSS-H634 | PRIMARY SUPERHEATER | 3RY SH OUTLET METAL TEMP (27P-NO2) | 3BSS-TE535 | 1 |  |  | 593 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 556 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAGAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoMjdQLU5PMik |  | 1
Boiler (BOL) | BSS | 3BSS-H635 | PRIMARY SUPERHEATER | 3RY SH OUTLET METAL TEMP (33P-NO2) | 3BSS-TE536 | 1 |  |  | 593 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 556 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAGgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoMzNQLU5PMik |  | 1
Boiler (BOL) | BSS | 3BSS-H636 | PRIMARY SUPERHEATER | 3RY SH OUTLET METAL TEMP (38P-NO2) | 3BSS-TE537 | 1 |  |  | 593 °C |  |  | 0 |  |  | 0-700degC | 0 |  | 556 °C |  | F1DPw1kUu10ziUaXEx2rIyo4pAGwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBPVVRMRVQgTUVUQUwgVEVNUCAoMzhQLU5PMik |  | 1
Boiler (BOL) | BSS | 3BSS-H637 | PRIMARY SUPERHEATER | 3RY SH OUTLET HEADER METAL TEMP (IN) | 3BSS-TE546 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-700degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pACQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBPVVRMRVQgSEVBREVSIE1FVEFMIFRFTVAgKElOKQ |  | 1
Boiler (BOL) | BSS | 3BSS-H638 | PRIMARY SUPERHEATER | 3RY SH OUTLET HEADER METAL TEMP (MID) | 3BSS-TE547 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-700degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pACgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBPVVRMRVQgSEVBREVSIE1FVEFMIFRFTVAgKE1JRCk |  | 1
Boiler (BOL) | BSS | 3BSS-H639 | PRIMARY SUPERHEATER | 3RY SH OUTLET HEADER METAL TEMP (OUT) | 3BSS-TE548 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-700degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pACwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLjNSWSBTSCBPVVRMRVQgSEVBREVSIE1FVEFMIFRFTVAgKE9VVCk |  | 1
Condensate Water (COND) | CAE | 3CAE-M010A | CONDENSER VACUUM PUMP A MOTOR
Condensate Water (COND) | CAE | 3CAE-M010B | CONDENSER VACUUM PUMP B MOTOR
Condensate Water (COND) | CAE | 3CAE-P010A | CONDENSER VACUUM PUMP A |  | NON DCS
Condensate Water (COND) | CAE | 3CAE-P010B | CONDENSER VACUUM PUMP B |  | NON DCS
Cooling Water (CW) | CCCW | 3CCCW-M010A | CCCWP A MOTOR | CCCWP A MTR CUR | 3CCCW-P010A-A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEEgTVRSIENVUg
Cooling Water (CW) | CCCW | 3CCCW-M010A | CCCWP A MOTOR | CCCWP A MTR WDG TEMP U | 3CCCW-TE003A | 1 |  |  | -999999 | 999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAkQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEEgTVRSIFdERyBURU1QIFU |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010A | CCCWP A MOTOR | CCCWP A MTR WDG TEMP V | 3CCCW-TE005A | 1 |  |  | -999999 | 999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAkgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEEgTVRSIFdERyBURU1QIFY |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010A | CCCWP A MOTOR | CCCWP A MTR WDG TEMP W | 3CCCW-TE007A | 1 |  |  | -999999 | 999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAkwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEEgTVRSIFdERyBURU1QIFc |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010A | CCCWP A MOTOR | CCCWP A MTR BRG 1 TEMP | 3CCCW-TE009A | 1 |  |  | -999999 |  |  |  |  | 100 | 0-200 degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAjgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEEgTVRSIEJSRyAxIFRFTVA |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010A | CCCWP A MOTOR | CCCWP A MTR BRG 2 TEMP | 3CCCW-TE010A | 1 | [7 empty] | 100 | 0-200 degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAjwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEEgTVRSIEJSRyAyIFRFTVA |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010A | CCCWP A MOTOR | BCP A MOTOR COOLER COOLING WTR TEMP | 3CCCW-TX531A | 1 |  |  | -999999 | -999999 |  |  |  | 999999 | 999999 |  |  | 0-200 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAtgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBBIE1PVE9SIENPT0xFUiBDT09MSU5HIFdUUiBURU1Q |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010A | CCCWP A MOTOR | BCP A HEAT BARRIER COOLING WTR OUTL TEMP | 3CCCW-TX532A | 1 |  |  | -999999 | -999999 |  |  |  | 999999 | 999999 |  |  | 0-20 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAtgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBBIE1PVE9SIENPT0xFUiBDT09MSU5HIFdUUiBURU1Q |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010B | CCCWP B MOTOR | CCCWP B MTR CUR | 3CCCW-P010B-A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAlgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEIgTVRSIENVUg
Cooling Water (CW) | CCCW | 3CCCW-M010B | CCCWP B MOTOR | CCCWP B MTR WDG TEMP U | 3CCCW-TE003B | 1 |  |  | -999999 | 999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAlwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEIgTVRSIFdERyBURU1QIFU |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010B | CCCWP B MOTOR | CCCWP B MTR WDG TEMP V | 3CCCW-TE005B | 1 |  |  | -999999 | 999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEIgTVRSIFdERyBURU1QIFY |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010B | CCCWP B MOTOR | CCCWP B MTR WDG TEMP W | 3CCCW-TE007B | 1 |  |  | -999999 | 999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEIgTVRSIFdERyBURU1QIFc |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010B | CCCWP B MOTOR | CCCWP B MTR BRG 1 TEMP | 3CCCW-TE009B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAlAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEIgTVRSIEJSRyAxIFRFTVA |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010B | CCCWP B MOTOR | CCCWP B MTR BRG 2 TEMP | 3CCCW-TE010B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAlQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIEIgTVRSIEJSRyAyIFRFTVA |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010B | CCCWP B MOTOR | BCP A MOTOR COOLER COOLING WTR TEMP | 3CCCW-TX531B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAugoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBCIE1PVE9SIENPT0xFUiBDT09MSU5HIFdUUiBURU1Q |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M010B | CCCWP B MOTOR | BCP A HEAT BARRIER COOLING WTR OUTL TEMP | 3CCCW-TX532B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAugoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBCIE1PVE9SIENPT0xFUiBDT09MSU5HIFdUUiBURU1Q |  | 1
Cooling Water (CW) | CCCW | 3CCCW-M090 | CCCW CHEMICAL DOOSING PUMP A MOTOR | CURRENT (A)
Cooling Water (CW) | CCCW | 3CCCW-M091 | CCCW CHEMICAL DOOSING PUMP A MOTOR | CCCWP A MTR BRG 1 TEMP
Cooling Water (CW) | CCCW | 3CCCW-M092 | CCCW CHEMICAL DOOSING PUMP A MOTOR | CCCWP A MTR BRG 2 TEMP
Cooling Water (CW) | CCCW | 3CCCW-P010A | CLOSED CYCLE COOLING WATER PUMP A | CCCW PMP A INL STR BEF&AFT PRESS | 3CCCW-PG001A
Cooling Water (CW) | CCCW | 3CCCW-M090 | CCCW CHEMICAL DOOSING PUMP B MOTOR | CURRENT(A)
Cooling Water (CW) | CCCW | 3CCCW-P010B | CLOSED CYCLE COOLING WATER PUMP B | CCCW PMP A OUTL PRESS | 3CCCW-PG002B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAmgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIE9VVEwgUFJFU1M
Cooling Water (CW) | CCCW | 3CCCW-P010A | CLOSED CYCLE COOLING WATER PUMP A | CCCWP OUTL PRESS | 3CCCW-PIX001 | 1 |  |  | 2025-07-06 |  |  | 0 |  | 999999 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIE9VVEwgUFJFU1M
Cooling Water (CW) | CCCW | 3CCCW-T010 | CCCW HEAD TANK | CCCWP OUTL TEMP | 3CCCW-TE001 | 1 |  |  | -999999 |  |  | 0 |  | 59 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1dQIE9VVEwgVEVNUA
Cooling Water (CW) | CCCW | 3CCCW-T010 | CCCW HEAD TANK | HD TK LVL | 3CCCW-LIX001 | 1 |  |  | -100 |  |  | 0 |  | 200 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAigsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1cgSEQgVEsgTFZM
Cooling Water (CW) | CCCW | 3CCCW-T010 | CCCW HEAD TANK | HX OUTL CCCW TEMP | 3CCCW-TE002 | 1 |  |  | -999999 |  |  | 0 |  | 59 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAiwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNDQ1cgSFggT1VUTCBDQ0NXIFRFTVA
Cooling Water (CW) | CCCW |  | BOILER CIRCULATING PUMP (BCP) A MOTOR COOLER | COOLING WATER TEMPERATURE | 3CCCW-TX531A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBBIE1PVE9SIENPT0xFUiBDT09MSU5HIFdUUiBURU1Q
Cooling Water (CW) | CCCW |  | BCP A HEAT BARRIER | COOLING WTR OUTL TEMP | 3CCCW-TX532A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAugoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBCIE1PVE9SIENPT0xFUiBDT09MSU5HIFdUUiBURU1Q
Cooling Water (CW) | CCCW |  | BOILER CIRCULATING PUMP (BCP) B MOTOR COOLER | COOLING WATER TEMPERATURE | 3CCCW-TX531B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAugoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBCIE1PVE9SIENPT0xFUiBDT09MSU5HIFdUUiBURU1Q
Cooling Water (CW) | CCCW |  | BCP B HEAT BARRIER | COOLING WTR OUTL TEMP | 3CCCW-TX532B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuQoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJDUCBCIEhFQVQgQkFSUklFUiBDT09MSU5HIFdUUiBPVVRMIFRFTVA
Cooling Water (CW) | CCCW | 3CCCW-P090 | CCCW CHEMICAL DOSING PUMP
Coal Handling (CH) | CHA | 00CHA | Boom Motor of Ship Unloader A
Coal Handling (CH) | CHA | 00CHA | Open close motor of Ship Unloader A
Coal Handling (CH) | CHA | 00CHA | Hoist motor of Ship Unloader A
Coal Handling (CH) | CHA | 00CHA | Trolley motor of Ship Unloader A
Coal Handling (CH) | CHA | 00CHA | Gantry motor of Ship Unloader A
Coal Handling (CH) | CHA | 00CHA | Boom Motor of Ship Unloader B
Coal Handling (CH) | CHA | 00CHA | Open close motor of Ship Unloader B
Coal Handling (CH) | CHA | 00CHA | Hoist motor of Ship Unloader B
Coal Handling (CH) | CHA | 00CHA | Trolley motor of Ship Unloader B
Coal Handling (CH) | CHA | 00CHA | Gantry motor of Ship Unloader B
Coal Handling (CH) | CHA | 00CHA-CV801A | Motor Conveyor 101 A
Coal Handling (CH) | CHA | 00CHA-CV802A | Motor Conveyor 102 A
Coal Handling (CH) | CHA | 00CHA-CV803A | Motor Conveyor 103 A
Coal Handling (CH) | CHA | 00CHA-CV801B | Motor Conveyor 101 B
Coal Handling (CH) | CHA | 00CHA-CV802B | Motor Conveyor 102 B
Coal Handling (CH) | CHA | 00CHA-CV803B | Motor Conveyor 103 B
Coal Handling (CH) | CHA | 00CHA-CV804 | Motor Conveyor 104
Coal Handling (CH) | CHB | 00CHB-CV805A | Motor Conveyor 105 A
Coal Handling (CH) | CHB | 00CHB-CV805B | Motor Conveyor 105 B
Coal Handling (CH) | CHB | 00CHB-SKR805A | Bucket Wheel Motor of Stacker Reclaimer A
Coal Handling (CH) | CHB | 00CHB-SKR805A | Boom Conveyor Motor of Stacker Reclaimer A
Coal Handling (CH) | CHB | 00CHB-SKR805A | Slewing Motor of Stacker Reclaimer A
Coal Handling (CH) | CHB | 00CHB-SKR805A | Gantry Motor of Stacker Reclaimer A
Coal Handling (CH) | CHB | 00CHB-SKR805B | Bucket Wheel Motor of Stacker Reclaimer B
Coal Handling (CH) | CHB | 00CHB-SKR805B | Boom Conveyor Motor of Stacker Reclaimer B
Coal Handling (CH) | CHB | 00CHB-SKR805B | Slewing Motor of Stacker Reclaimer B
Coal Handling (CH) | CHB | 00CHB-SKR805B | Gantry Motor of Stacker Reclaimer B
Chlorination (CP) | CL | 00CL-M001A | CHLORINATION SYSTEM SEAWATER BOOSTER PUMP A MOTOR
Chlorination (CP) | CL | 00CL-M001B | CHLORINATION SYSTEM SEAWATER BOOSTER PUMP B MOTOR
Chlorination (CP) | CL | 00CL-M002A | CHLORINATION SYSTEM SODIUM HYPOCHLORITE DOSING PUMP A MOTOR
Chlorination (CP) | CL | 00CL-M002B | CHLORINATION SYSTEM SODIUM HYPOCHLORITE DOSING PUMP B MOTOR
Chlorination (CP) | CL | 00CL-M003 | CHLORINATION SYSTEM ACID PUMP MOTOR
Chlorination (CP) | CL | 00CL-M004A | CHLORINATION SYSTEM CHEMICAL SUMP PUMP A MOTOR
Chlorination (CP) | CL | 00CL-M004B | CHLORINATION SYSTEM CHEMICAL SUMP PUMP B MOTOR
Chlorination (CP) | CL | 00CL-M005A | CHLORINATION TRANSFORMER COOLING FAN 1A
Chlorination (CP) | CL | 00CL-M005B | CHLORINATION TRANSFORMER COOLING FAN 1B
Chlorination (CP) | CL | 00CL-M006A | CHLORINATION TRANSFORMER COOLING FAN 2A
Chlorination (CP) | CL | 00CL-M006B | CHLORINATION TRANSFORMER COOLING FAN 2B
Chlorination (CP) | CL | 00CL-M007A | CHLORINATION TRANSFORMER COOLING FAN 3A
Chlorination (CP) | CL | 00CL-M007B | CHLORINATION TRANSFORMER COOLING FAN 3B
Chlorination (CP) | CL | 00CL-M008A | CHLORINATION TRANSFORMER COOLING FAN 4A
Chlorination (CP) | CL | 00CL-M008B | CHLORINATION TRANSFORMER COOLING FAN 4B
Chlorination (CP) | CL | 00CL-M009A | CHLORINATION TRANSFORMER COOLING FAN 5A
Chlorination (CP) | CL | 00CL-M009B | CHLORINATION TRANSFORMER COOLING FAN 5B
Chlorination (CP) | CL | 00CL-P001A | CHLORINATION SYSTEM SEAWATER BOOSTER PUMP A | SWBP A INL PRESS GA | 00CL-PGS001 | [14 empty] | 0
Chlorination (CP) | CL | 00CL-P001A | CHLORINATION SYSTEM SEAWATER BOOSTER PUMP A | SWBP A OUTL PRESS GA | 00CL-PG001A | [14 empty] | 0
Chlorination (CP) | CL | 00CL-P001B | CHLORINATION SYSTEM SEAWATER BOOSTER PUMP B | SWBP B OUTL PRESS GA | 00CL-PG001B | [14 empty] | 0
Chlorination (CP) | CL | 00CL-P002A | CHLORINATION SYSTEM SODIUM HYPOCHLORITE DOSING PUMP A | NaOCl DOS PMP A INL PRESS GA | 00CL-PG003A | [14 empty] | 0
Chlorination (CP) | CL | 00CL-P002A | CHLORINATION SYSTEM SODIUM HYPOCHLORITE DOSING PUMP A | NaOCl DOS PMP A OUTL PRESS GA | 00CL-PG004A | [14 empty] | 0
Chlorination (CP) | CL | 00CL-P002B | CHLORINATION SYSTEM SODIUM HYPOCHLORITE DOSING PUMP B | NaOCl DOS PMP B INL PRESS GA | 00CL-PG003B | [14 empty] | 0
Chlorination (CP) | CL | 00CL-P002B | CHLORINATION SYSTEM SODIUM HYPOCHLORITE DOSING PUMP B | NaOCl DOS PMP B OUTL PRESS GA | 00CL-PG004B | [14 empty] | 0
Chlorination (CP) | CL | 00CL-P003 | CHLORINATION SYSTEM ACID PUMP | ACID PMP OUTL PRESS GA | 00CL-PG005 | [14 empty] | 0
Chlorination (CP) | CL | 00CL-P004A | CHLORINATION SYSTEM CHEMICAL SUMP PUMP A | CHEM SMPP A OUTL PRESS GA | 00CL-PG006A | [14 empty] | 0
Chlorination (CP) | CL | 00CL-P004B | CHLORINATION SYSTEM CHEMICAL SUMP PUMP B | CHEM SMPP B OUTL PRESS GA | 00CL-PG006B | [14 empty] | 0
Chlorination (CP) | CL | 00CL-XR001A | CHLORINATION SYSTEM TRANSFORMER/RECTIFIER A | 10KV SB A CLN SYS A CB CUR | 00CL-XR004A-A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pADQAAAAS1RKQi1LSTAwLVBJMVxUSkIxLjEwS1YgU0IgQSBDSExPUkkgQSAgQ1VSUkVOVA
Chlorination (CP) | CL | 00CL-XR001B | CHLORINATION SYSTEM TRANSFORMER/RECTIFIER B | 10KV SB A CLN SYS B CB CUR | 00CL-XR004B-A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAFQAAAAS1RKQi1LSTAwLVBJMVxUSkIxLjEwS1YgU0IgQiBDSExPUkkgIEIgQ1VSUkVOVA
Chlorination (CP) | CL | 00CL-Z001A | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR A1 | CLN SYS NaOCl GEN INL FLW | 00CL-FIX001A | [14 empty] | 0
Chlorination (CP) | CL | 00CL-Z001B | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR B1 | CLN SYS NaOCl GEN INL FLW | 00CL-FIX001B | [14 empty] | 0
Chlorination (CP) | CL | 00CL-Z001C | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR C1 | CLN SYS NaOCl GEN INL FLW | 00CL-FIX001C | [14 empty] | 0
Chlorination (CP) | CL | 00CL-Z001D | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR D1 | CLN SYS NaOCl GEN INL FLW | 00CL-FIX001D | [14 empty] | 0
Chlorination (CP) | CL | 00CL-Z002A | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR A2
Chlorination (CP) | CL | 00CL-Z002B | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR B2
Chlorination (CP) | CL | 00CL-Z002C | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR C2
Chlorination (CP) | CL | 00CL-Z002D | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR D2
Condensate Water (COND) | CO | 3CO-H001 | CONDENSER | COND WTR PRESS A | 3CO-PIX002A | 1 |  |  |  | 17 | 15.5 |  |  | 99999999 | 0-40barg |  |  | 20barg |  | F1DPw1kUu10ziUaXEx2rIyo4pA8AsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPTkQgV1RSIFBSRVNTIEE |  | 1
Condensate Water (COND) | CO | 3CO-H001 | CONDENSER | COND WTR PRESS B | 3CO-PIX002B | 1 |  |  |  | 17 | 15.5 |  |  | 99999999 | 0-40barg |  |  | 20barg |  | F1DPw1kUu10ziUaXEx2rIyo4pA8QsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPTkQgV1RSIFBSRVNTIEI |  | 1
Condensate Water (COND) | CO | 3CO-H001 | CONDENSER | CONDR HW TEMP | 3CO-TE001 | 1 | [8 empty] | 0-100degC |  |  | 41 |  | F1DPw1kUu10ziUaXEx2rIyo4pA-gsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPTkRSIEhXIFRFTVA |  | 1
Condensate Water (COND) | CO | 3CO-H001 | CONDENSER | GLND STM CONDR OUTL COND WTR FLW | 3CO-FIX001 | 1 | t/h | [7 empty] | 0-2500 t/h |  |  | 1641t/h |  | F1DPw1kUu10ziUaXEx2rIyo4pANA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdMTkQgU1RNIENPTkRSIE9VVEwgQ09ORCBXVFIgRkxX
Condensate Water (COND) | CO | 3CO-H001 | CONDENSER | GLND STM CONDR INL COND TEMP | 3CO-TG001
Condensate Water (COND) | CO | 3CO-H010 | LP FEEDWATER HEATER NO.1 | LP FW HTR 1 OUTL COND WTR TEMP | 3CO-TE003 | 1 | [8 empty] | 0-150degC |  |  | 59 |  | F1DPw1kUu10ziUaXEx2rIyo4pA6w0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQIEZXIEhUUiAxIE9VVEwgQ09ORCBXVFIgVEVNUA |  | 1
Condensate Water (COND) | CO | 3CO-H020 | LP FEEDWATER HEATER NO.2 | LP FW HTR 2 OUTL COND WTR TEMP | 3CO-TE004 | 1 | [8 empty] | 0-200degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA8w0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQIEZXIEhUUiAyIE9VVEwgQ09ORCBXVFIgVEVNUA |  | 1
Condensate Water (COND) | CO | 3CO-H030 | LP FEEDWATER HEATER NO.3 | LP FW HTR 3 OUTL COND WTR TEMP | 3CO-TT003
Condensate Water (COND) | CO | 3CO-M001A | CONDENSATE EXTRACTION PUMP A MOTOR | CEP A MTR WDG TEMP U | 3CO-TE006A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 120 | 155 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pArQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBBIE1UUiBXREcgVEVNUCBV |  | 1
Condensate Water (COND) | CO | 3CO-M001A | CONDENSATE EXTRACTION PUMP A MOTOR | CEP A MTR WDG TEMP V | 3CO-TE008A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 120 | 155 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pArgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBBIE1UUiBXREcgVEVNUCBW |  | 1
Condensate Water (COND) | CO | 3CO-M001A | CONDENSATE EXTRACTION PUMP A MOTOR | CEP A MTR WDG TEMP W | 3CO-TE010A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 120 | 155 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pArwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBBIE1UUiBXREcgVEVNUCBX |  | 1
Condensate Water (COND) | CO | 3CO-M001A | CONDENSATE EXTRACTION PUMP A MOTOR | CEP A MTR BRG 1 TEMP | 3CO-TE012A | 1 |  |  | -999999 |  |  | 0 |  | 100 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAqgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBBIE1UUiBCUkcgMSBURU1Q |  | 1
Condensate Water (COND) | CO | 3CO-M001A | CONDENSATE EXTRACTION PUMP A MOTOR | CEP A MTR BRG 2 TEMP | 3CO-TE013A | 1 |  |  | -999999 |  |  | 0 |  | 95 | 0-200degC | 0 |  | 38.8 |  | F1DPw1kUu10ziUaXEx2rIyo4pAqwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBBIE1UUiBCUkcgMiBURU1Q |  | 1
Condensate Water (COND) | CO | 3CO-M001A | CONDENSATE EXTRACTION PUMP A MOTOR | CEP A MTR CUR | 3CO-P001A-A | 1 | [8 empty] | 0-750A |  |  | 0 |  | F1DPw1kUu10ziUaXEx2rIyo4pArAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBBIE1UUiBDVVI |  | 1
Condensate Water (COND) | CO | 3CO-M001B | CONDENSATE EXTRACTION PUMP B MOTOR | CEP B MTR WDG TEMP U | 3CO-TE006B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 120 | 155 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAtAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBCIE1UUiBXREcgVEVNUCBV |  | 1
Condensate Water (COND) | CO | 3CO-M001B | CONDENSATE EXTRACTION PUMP B MOTOR | CEP B MTR WDG TEMP V | 3CO-TE008B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 120 | 155 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAtQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBCIE1UUiBXREcgVEVNUCBW |  | 1
Condensate Water (COND) | CO | 3CO-M001B | CONDENSATE EXTRACTION PUMP B MOTOR | CEP B MTR WDG TEMP W | 3CO-TE010B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 120 | 155 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAtgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBCIE1UUiBXREcgVEVNUCBX |  | 1
Condensate Water (COND) | CO | 3CO-M001B | CONDENSATE EXTRACTION PUMP B MOTOR | CEP B MTR BRG 1 TEMP | 3CO-TE012B | 0 |  |  | -999999 |  |  | 0 |  | 100 | 0-200degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAsQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBCIE1UUiBCUkcgMSBURU1Q |  | 1
Condensate Water (COND) | CO | 3CO-M001B | CONDENSATE EXTRACTION PUMP B MOTOR | CEP B MTR BRG 2 TEMP | 3CO-TE013B | 1 |  |  | -999999 |  |  | 0 |  | 95 | 0-200degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAsgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBCIE1UUiBCUkcgMiBURU1Q |  | 1
Condensate Water (COND) | CO | 3CO-M001B | CONDENSATE EXTRACTION PUMP B MOTOR | CEP B MTR CUR | 3CO-P001B-A | 1 | [8 empty] | 0-750A |  |  | 85 |  | F1DPw1kUu10ziUaXEx2rIyo4pAswsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBCIE1UUiBDVVI |  | 1
Condensate Water (COND) | CO | 3CO-P001A | CONDENSATE EXTRACTION PUMP A | CEP A INL STR DP | 3CO-DPIX001A | 1 |  |  | -999999 |  |  | 0 |  | 56 | 0-1000 mbar | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAqQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBBIElOTCBTVFIgRFA |  | 1
Condensate Water (COND) | CO | 3CO-P001A | CONDENSATE EXTRACTION PUMP A | CEP A OUTL PRESS | 3CO-PG002A
Condensate Water (COND) | CO | 3CO-P001B | CONDENSATE EXTRACTION PUMP B | CEP B INL STR DP | 3CO-DPIX001B | 1 |  |  | -999999 |  |  | 0 |  | 56 | 0-1000 mbar | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAsAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBCIElOTCBTVFIgRFA |  | 1
Condensate Water (COND) | CO | 3CO-P001B | CONDENSATE EXTRACTION PUMP B | CEP B OUTL PRESS | 3CO-PG002B
Boiler (BOL) | CRH |  | COLD REHEATER | HP FW HTR 6 CRH EXTR STM TEMP | 3CRH-TT001
Boiler (BOL) | CW | 3CW-M010A | CIRCULATING WATER PUMP A MOTOR | CWP A MTR AIR OUTL TEMP | 3CW-TE003A | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-200degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pANAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBPVVRMIENMRyBBSVIgVEVNUA
Boiler (BOL) | CW | 3CW-M010A | CIRCULATING WATER PUMP A MOTOR | CWP A MTR WDG TEMP U | 3CW-TE004A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pANgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBXREcgVEVNUCBV |  | 1
Boiler (BOL) | CW | 3CW-M010A | CIRCULATING WATER PUMP A MOTOR | CWP A MTR WDG TEMP U | 3CW-TE005A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pANgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBXREcgVEVNUCBV
Boiler (BOL) | CW | 3CW-M010A | CIRCULATING WATER PUMP A MOTOR | CWP A MTR WDG TEMP V | 3CW-TE006A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pANwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBXREcgVEVNUCBW |  | 1
Boiler (BOL) | CW | 3CW-M010A | CIRCULATING WATER PUMP A MOTOR | CWP A MTR WDG TEMP V | 3CW-TE007A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pANwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBXREcgVEVNUCBW
Boiler (BOL) | CW | 3CW-M010A | CIRCULATING WATER PUMP A MOTOR | CWP A MTR WDG TEMP W | 3CW-TE008A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAOAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBXREcgVEVNUCBX |  | 1
Boiler (BOL) | CW | 3CW-M010A | CIRCULATING WATER PUMP A MOTOR | CWP A MTR WDG TEMP W | 3CW-TE009A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAOAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBXREcgVEVNUCBX
Boiler (BOL) | CW | 3CW-M010A | CIRCULATING WATER PUMP A MOTOR | CWP A MTR BRG1 TEMP | 3CW-TE010A | 1 |  |  | -999999 |  |  | 0 |  | 100 | 0-200degC | 0 |  | Now: 43 |  | F1DPw1kUu10ziUaXEx2rIyo4pAMAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBCUkcgMSBURU1Q |  | 1
Boiler (BOL) | CW | 3CW-M010A | CIRCULATING WATER PUMP A MOTOR | CWP A MTR THRUST BRG TEMP | 3CW-TE011A | 1 |  |  | -999999 |  |  | 0 |  | 95 | 0-200degC | 0 |  | Now: 85.5 |  | F1DPw1kUu10ziUaXEx2rIyo4pANQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBUSFJTVCBCUkcgTUVUIFRFTVA |  | 1
Boiler (BOL) | CW | 3CW-M010A | CIRCULATING WATER PUMP A MOTOR | CWP A MTR BRG2 TEMP | 3CW-TE012A | 1 | [7 empty] | 95 | 0-200degC |  |  | Now: 75.5 |  | F1DPw1kUu10ziUaXEx2rIyo4pAMQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBCUkcgMiBURU1Q |  | 1
Boiler (BOL) | CW | 3CW-M010A | CIRCULATING WATER PUMP A MOTOR | CWP MTR CUR | 3CW-P010A-A | 1 | [8 empty] | 0-300-1500A |  |  | Now: 248A |  | F1DPw1kUu10ziUaXEx2rIyo4pAMgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBDVVI |  | 1
Boiler (BOL) | CW | 3CW-M010B | CIRCULATING WATER PUMP B MOTOR | CWP B MTR AIR OUTL TEMP | 3CW-TE003B | 1 |  |  | -999999 |  |  | 0 |  | 80 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAPwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBPVVRMIENMRyBBSVIgVEVNUA
Boiler (BOL) | CW | 3CW-M010B | CIRCULATING WATER PUMP B MOTOR | CWP B MTR WDG TEMP U | 3CW-TE004B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAQQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBXREcgVEVNUCBV |  | 1
Boiler (BOL) | CW | 3CW-M010B | CIRCULATING WATER PUMP B MOTOR | CWP B MTR WDG TEMP U | 3CW-TE005B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAQQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBXREcgVEVNUCBV
Boiler (BOL) | CW | 3CW-M010B | CIRCULATING WATER PUMP B MOTOR | CWP B MTR WDG TEMP V | 3CW-TE006B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAQgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBXREcgVEVNUCBW |  | 1
Boiler (BOL) | CW | 3CW-M010B | CIRCULATING WATER PUMP B MOTOR | CWP B MTR WDG TEMP V | 3CW-TE007B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAQgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBXREcgVEVNUCBW
Boiler (BOL) | CW | 3CW-M010B | CIRCULATING WATER PUMP B MOTOR | CWP B MTR WDG TEMP W | 3CW-TE008B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAQwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBXREcgVEVNUCBX |  | 1
Boiler (BOL) | CW | 3CW-M010B | CIRCULATING WATER PUMP B MOTOR | CWP B MTR WDG TEMP W | 3CW-TE009B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAQwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBXREcgVEVNUCBX |  | 1
Boiler (BOL) | CW | 3CW-M010B | CIRCULATING WATER PUMP B MOTOR | CWP B MTR BRG1 TEMP | 3CW-TE010B | 1 |  |  | -999999 |  |  | 0 |  | 100 | 0-200degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAOwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBCUkcgMSBURU1Q |  | 1
Boiler (BOL) | CW | 3CW-M010B | CIRCULATING WATER PUMP B MOTOR | CWP B MTR THRUST BRG TEMP | 3CW-TE011B | 1 |  |  | -999999 |  |  | 0 |  | 95 | 0-200degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAQAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBUSFJTVCBCUkcgTUVUIFRFTVA |  | 1
Boiler (BOL) | CW | 3CW-M010B | CIRCULATING WATER PUMP B MOTOR | CWP B MTR BRG2 TEMP | 3CW-TE012B | 1 | t/h | [7 empty] | 0-200degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAPAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBCUkcgMiBURU1Q |  | 1
Boiler (BOL) | CW | 3CW-M010B | CIRCULATING WATER PUMP B MOTOR | CWP B MTR CUR | 3CW-P010B-A | 1 | [8 empty] | 0-300-1500A |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAPQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBDVVI |  | 1
Boiler (BOL) | CW | 3CW-M011A | CIRCULATING WATER PUMP A MOTOR COOLING WATER BOOSTER PUMP MOTOR
Boiler (BOL) | CW | 3CW-M011B | CIRCULATING WATER PUMP B MOTOR COOLING WATER BOOSTER PUMP MOTOR
Boiler (BOL) | CW | 3CW-M020A | SEAWATER BOOSTER PUMP A MOTOR | SWBP A MTR CUR | 3CW-P020A-A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBNVFIgQ1VS |  | 1
Boiler (BOL) | CW | 3CW-M020A | SEAWATER BOOSTER PUMP A MOTOR | SWBP A MTR WDG TEMP U | 3CW-TE013A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBNVFIgV0RHIFRFTVAgVQ
Boiler (BOL) | CW | 3CW-M020A | SEAWATER BOOSTER PUMP A MOTOR | SWBP A MTR WDG TEMP V | 3CW-TE015A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBNVFIgV0RHIFRFTVAgVg
Boiler (BOL) | CW | 3CW-M020A | SEAWATER BOOSTER PUMP A MOTOR | SWBP A MTR WDG TEMP W | 3CW-TE017A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBNVFIgV0RHIFRFTVAgVw
Boiler (BOL) | CW | 3CW-M020A | SEAWATER BOOSTER PUMP A MOTOR | SWBP A MTR BRG 1 TEMP | 3CW-TE019A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAew8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBNVFIgQlJHIDEgVEVNUA
Boiler (BOL) | CW | 3CW-M020A | SEAWATER BOOSTER PUMP A MOTOR | SWBP A MTR BRG 2 TEMP | 3CW-TE020A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBNVFIgQlJHIDIgVEVNUA
Boiler (BOL) | CW | 3CW-M020B | SEAWATER BOOSTER PUMP B MOTOR | SWBP B MTR CUR | 3CW-P020B-A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBNVFIgQ1VS |  | 1
Boiler (BOL) | CW | 3CW-M020B | SEAWATER BOOSTER PUMP B MOTOR | SWBP B MTR WDG TEMP U | 3CW-TE013B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBNVFIgV0RHIFRFTVAgVQ
Boiler (BOL) | CW | 3CW-M020B | SEAWATER BOOSTER PUMP B MOTOR | SWBP B MTR WDG TEMP V | 3CW-TE015B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBNVFIgV0RHIFRFTVAgVg
Boiler (BOL) | CW | 3CW-M020B | SEAWATER BOOSTER PUMP B MOTOR | SWBP B MTR WDG TEMP W | 3CW-TE017B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAiA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBNVFIgV0RHIFRFTVAgVw
Boiler (BOL) | CW | 3CW-M020B | SEAWATER BOOSTER PUMP B MOTOR | SWBP B MTR BRG 1 TEMP | 3CW-TE019B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBNVFIgQlJHIDEgVEVNUA
Boiler (BOL) | CW | 3CW-M020B | SEAWATER BOOSTER PUMP B MOTOR | SWBP B MTR BRG 2 TEMP | 3CW-TE020B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBNVFIgQlJHIDIgVEVNUA
Boiler (BOL) | CW | 3CW-P010A | CIRCULATING WATER PUMP A | CWP A OUTL PRESS | 3CW-PIX001A | 1 | [8 empty] | -1-7 barg |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAOQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE9VVEwgUFJFU1M |  | 1
Boiler (BOL) | CW | 3CW-P010B | CIRCULATING WATER PUMP B | CWP B OUTL PRESS | 3CW-PIX001B | 1 | [8 empty] | -1-7 barg |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pARAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE9VVEwgUFJFU1M |  | 1
Boiler (BOL) | CW | 3CW-P011A | CIRCULATING WATER PUMP A MOTOR COOLING WATER BOOSTER PUMP | CWP A MTR CW FLW | 3CW-FIX001A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAMwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBDVyBGTFc
Boiler (BOL) | CW | 3CW-P011B | CIRCULATING WATER PUMP B MOTOR COOLING WATER BOOSTER PUMP | CWP B MTR CW FLW | 3CW-FIX001B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAPgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBDVyBGTFc
Boiler (BOL) | CW | 3CW-P020A | SEAWATER BOOSTER PUMP A | SWBP A DP | 3CW-DPIX002A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAeQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBEUA
Boiler (BOL) | CW | 3CW-P020A | SEAWATER BOOSTER PUMP A | SWBP A FLOW | 3PFC_OUT_TAG8 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAeg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBGTE9X
Boiler (BOL) | CW | 3CW-P020B | SEAWATER BOOSTER PUMP B | SWBP B DP | 3CW-DPIX002B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBEUA
Boiler (BOL) | CW | 3CW-P020B | SEAWATER BOOSTER PUMP B | SWBP B FLOW | 3PFC_OUT_TAG9 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBGTE9X
Plant Control (PC) | DCS | NOT ELIGIBLE | Distributed Control System
Boiler (BOL) | DM | NOT ELIGIBLE
Water Treatment Plant (WTP) | DMW | 00DMW-A385A | AIR DRYER A
Water Treatment Plant (WTP) | DMW | 00DMW-A385B | AIR DRYER B
Water Treatment Plant (WTP) | DMW | 00DMW-C375A | AIR COMPRESSOR A
Water Treatment Plant (WTP) | DMW | 00DMW-C375B | AIR COMPRESSOR B
Water Treatment Plant (WTP) | DMW | 00DMW-M110A | PRETREATED WATER PUMP A MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M110B | PRETREATED WATER PUMP B MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M190A | REGENERATION PUMP A MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M190B | REGENERATION PUMP B MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M200A | DMW NaOH UNLOADING PUMP A MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M200B | DMW NaOH UNLOADING PUMP B MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M220A | DMW NaOH TRANSFER PUMP A MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M220B | DMW NaOH TRANSFER PUMP B MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M300A | DMW HCl UNLOADING PUMP A MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M300B | DMW HCl UNLOADING PUMP B MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M320A | DMW HCl TRANSFER PUMP A MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M320B | DMW HCl TRANSFER PUMP B MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M360A | MIXED BED AIR BLOWER A MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M360B | MIXED BED AIR BLOWER B MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M370A | DMW NEUTRALIZATION PUMP A MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M370B | DMW NEUTRALIZATION PUMP B MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M375A | AIR COMPRESSOR A MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-M375B | AIR COMPRESSOR B MOTOR
Water Treatment Plant (WTP) | DMW | 00DMW-P100 | RESIN BACKWASH / TRANSFER PUMP
Water Treatment Plant (WTP) | DMW | 00DMW-F360A | MIXED BED AIR BLOWER A | MIXED BED AIR BLOWER A OUTLET PRESSURE GAUGE | 00DMW-PG361A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-F360B | MIXED BED AIR BLOWER B | MIXED BED AIR BLOWER B OUTLET PRESSURE GAUGE | 00DMW-PG361B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P110A | PRETREATED WATER PUMP A | PRETREATED WATER PUMP A INLET PRESSURE GAUGE | 00DMW-PG111A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P110A | PRETREATED WATER PUMP A | PRETREATED WATER PUMP A OUTLET PRESSURE GAUGE | 00DMW-PG112A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P110B | PRETREATED WATER PUMP B | PRETREATED WATER PUMP B INLET PRESSURE GAUGE | 00DMW-PG111B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P110B | PRETREATED WATER PUMP B | PRETREATED WATER PUMP B OUTLET PRESSURE GAUGE | 00DMW-PG112B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P190A | REGENERATION PUMP A | REGENERATION PUMP A INLET PRESSURE GAUGE | 00DMW-PG192A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P190A | REGENERATION PUMP A | REGENERATION PUMP OUTLET A PRESSURE GAUGE | 00DMW-PG193A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P190B | REGENERATION PUMP B | REGENERATION PUMP B INLET PRESSURE GAUGE | 00DMW-PG192B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P190B | REGENERATION PUMP B | REGENERATION PUMP B OUTLET PRESSURE GAUGE | 00DMW-PG193B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P200A | DMW NaOH UNLOADING PUMP A | DMW NaOH UNLOADING PUMP A INLET PRESSURE GAUGE | 00DMW-PG202A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P200A | DMW NaOH UNLOADING PUMP A | DMW NaOH UNLOADING PUMP A OUTLET PRESSURE GAUGE | 00DMW-PG203A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P200B | DMW NaOH UNLOADING PUMP B | DMW NaOH UNLOADING PUMP B INLET PRESSURE GAUGE | 00DMW-PG202B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P200B | DMW NaOH UNLOADING PUMP B | DMW NaOH UNLOADING PUMP B OUTLET PRESSURE GAUGE | 00DMW-PG203B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P220A | DMW NaOH TRANSFER PUMP A | DMW NaOH TRANSFER PUMP A INLET PRESSURE GAUGE | 00DMW-PG222A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P220A | DMW NaOH TRANSFER PUMP A | DMW NaOH TRANSFER PUMP A OUTLET PRESSURE GAUGE | 00DMW-PG223A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P220B | DMW NaOH TRANSFER PUMP B | DMW NaOH TRANSFER PUMP B INLET PRESSURE GAUGE | 00DMW-PG222B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P220B | DMW NaOH TRANSFER PUMP B | DMW NaOH TRANSFER PUMP B OUTLET PRESSURE GAUGE | 00DMW-PG223B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P300A | DMW HCl UNLOADING PUMP A | DMW HCl UNLOADING PUMP A INLET PRESSURE GAUGE | 00DMW-PG302A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P300A | DMW HCl UNLOADING PUMP A | DMW HCl UNLOADING PUMP A OUTLET PRESSURE GAUGE | 00DMW-PG303A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P300B | DMW HCl UNLOADING PUMP B | DMW HCl UNLOADING PUMP B INLET PRESSURE GAUGE | 00DMW-PG302B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P300B | DMW HCl UNLOADING PUMP B | DMW HCl UNLOADING PUMP B OUTLET PRESSURE GAUGE | 00DMW-PG303B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P320A | DMW HCl TRANSFER PUMP A | DMW HCl TRANSFER PUMP A INLET PRESSURE GAUGE | 00DMW-PG322A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P320A | DMW HCl TRANSFER PUMP A | DMW HCl TRANSFER PUMP A OUTLET PRESSURE GAUGE | 00DMW-PG323A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P320B | DMW HCl TRANSFER PUMP B | DMW HCl TRANSFER PUMP B INLET PRESSURE GAUGE | 00DMW-PG322B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P320B | DMW HCl TRANSFER PUMP B | DMW HCl TRANSFER PUMP B OUTLET PRESSURE GAUGE | 00DMW-PG323B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P370A | DMW NEUTRALIZATION PUMP A | DMW NEUTRALIZATION PUMP A INLET PRESSURE GAUGE | 00DMW-PG367A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P370A | DMW NEUTRALIZATION PUMP A | DMW NEUTRALIZATION PUMP A OUTLET PRESSURE GAUGE | 00DMW-PG368A | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P370B | DMW NEUTRALIZATION PUMP B | DMW NEUTRALIZATION PUMP B INLET PRESSURE GAUGE | 00DMW-PG367B | [14 empty] | 0
Water Treatment Plant (WTP) | DMW | 00DMW-P370B | DMW NEUTRALIZATION PUMP B | DMW NEUTRALIZATION PUMP B OUTLET PRESSURE GAUGE | 00DMW-PG368B | [14 empty] | 0
Boiler (BOL) | DP | 3DP-FDR711A | COAL FEEDER A | COAL FEEDER COAL FLOW | 3DP-HSIG311 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-100t/h | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA2wsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEEgQ09BTCBGTE9X |  | 1
Boiler (BOL) | DP | 3DP-FDR711B | COAL FEEDER B | COAL FEEDER COAL FLOW | 3DP-HSIG321 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-100t/h | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA3QsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEIgQ09BTCBGTE9X |  | 1
Boiler (BOL) | DP | 3DP-FDR711C | COAL FEEDER C | COAL FEEDER COAL FLOW | 3DP-HSIG331 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-100t/h | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA3wsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEMgQ09BTCBGTE9X |  | 1
Boiler (BOL) | DP | 3DP-FDR711D | COAL FEEDER D | COAL FEEDER COAL FLOW | 3DP-HSIG341 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-100t/h | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA4QsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEQgQ09BTCBGTE9X |  | 1
Boiler (BOL) | DP | 3DP-FDR711E | COAL FEEDER E | COAL FEEDER COAL FLOW | 3DP-HSIG351 | 1 | t/h |  | -999999 |  |  | 0 |  | 999999 | 0-100t/h | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA4wsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEUgQ09BTCBGTE9X |  | 1
Boiler (BOL) | DP | 3DP-FDR711F | COAL FEEDER F | COAL FEEDER COAL FLOW | 3DP-HSIG361 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-100t/h | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA5QsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEYgQ09BTCBGTE9X |  | 1
Boiler (BOL) | DP | 3DP-FDR711A | COAL FEEDER A | COAL FEEDER TEMP | 3DP-TX501A | 1 |  |  | -999999 |  |  | 0 |  | 90 | 0-150degC | 0 |  | 38 |  | F1DPw1kUu10ziUaXEx2rIyo4pA3AsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEEgVEVNUA |  | 1
Boiler (BOL) | DP | 3DP-FDR711B | COAL FEEDER B | COAL FEEDER TEMP | 3DP-TX501B | 1 |  |  | -999999 |  |  | 0 |  | 90 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA3gsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEIgVEVNUA |  | 1
Boiler (BOL) | DP | 3DP-FDR711C | COAL FEEDER C | COAL FEEDER TEMP | 3DP-TX501C | 1 |  |  | -999999 |  |  | 0 |  | 90 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA4AsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEMgVEVNUA |  | 1
Boiler (BOL) | DP | 3DP-FDR711D | COAL FEEDER D | COAL FEEDER TEMP | 3DP-TX501D | 1 |  |  | -999999 |  |  | 0 |  | 90 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA4gsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEQgVEVNUA |  | 1
Boiler (BOL) | DP | 3DP-FDR711E | COAL FEEDER E | COAL FEEDER TEMP | 3DP-TX501E | 1 |  |  | -999999 |  |  | 0 |  | 90 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA5AsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEUgVEVNUA |  | 1
Boiler (BOL) | DP | 3DP-FDR711F | COAL FEEDER F | COAL FEEDER TEMP | 3DP-TX501F | 1 |  |  | -999999 |  |  | 0 |  | 90 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA5gsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgRkVFREVSIEYgVEVNUA |  | 1
Boiler (BOL) | DP | 3DP-M711A | COAL FEEDER A MOTOR
Boiler (BOL) | DP | 3DP-M711B | COAL FEEDER B MOTOR
Boiler (BOL) | DP | 3DP-M711C | COAL FEEDER C MOTOR
Boiler (BOL) | DP | 3DP-M711D | COAL FEEDER D MOTOR
Boiler (BOL) | DP | 3DP-M711E | COAL FEEDER E MOTOR
Boiler (BOL) | DP | 3DP-M711F | COAL FEEDER F MOTOR
Boiler (BOL) | DP | 3DP-M712A | COAL FEEDER A CLEANOUT CONVEYOR MOTOR
Boiler (BOL) | DP | 3DP-M712B | COAL FEEDER B CLEANOUT CONVEYOR MOTOR
Boiler (BOL) | DP | 3DP-M712C | COAL FEEDER C CLEANOUT CONVEYOR MOTOR
Boiler (BOL) | DP | 3DP-M712D | COAL FEEDER D CLEANOUT CONVEYOR MOTOR
Boiler (BOL) | DP | 3DP-M712E | COAL FEEDER E CLEANOUT CONVEYOR MOTOR
Boiler (BOL) | DP | 3DP-M712F | COAL FEEDER F CLEANOUT CONVEYOR MOTOR
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | COAL PULV A MOT CUR | 3DP-BM731A-A | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA6AsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBBIE1PVCBDVVI |  | 1
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | PULVERIZER A SHAFT BRG TEMP | 3DP-TE705A | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA0g4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQSBNT1RPUiBCRUFSSU5HIFRFTVAtREU |  | 1
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | PULVERIZER A THRUST BRG TEMP | 3DP-TE706A | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA0w4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQSBNT1RPUiBCRUFSSU5HIFRFTVAtTkRF |  | 1
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | PULV A MOTOR WINDING TEMP-U1 | 3DP-TE731A | 1 | [5 empty] | 0 |  | 160°C (trip) | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAlw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQSBNT1RPUiBXSU5ESU5HIFRFTVAtVTE |  | 1
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | PULV A MOTOR WINDING TEMP-U2 | 3DP-TE732A | 1 | [5 empty] | 0 |  | 160°C (trip) | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAmA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQSBNT1RPUiBXSU5ESU5HIFRFTVAtVTI |  | 1
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | PULV A MOTOR WINDING TEMP-V1 | 3DP-TE733A | 1 | [5 empty] | 0 |  | 160°C (trip) | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAmQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQSBNT1RPUiBXSU5ESU5HIFRFTVAtVjE |  | 1
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | PULV A MOTOR WINDING TEMP-V2 | 3DP-TE734A | 1 | [5 empty] | 0 |  | 160°C (trip) | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAmg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQSBNT1RPUiBXSU5ESU5HIFRFTVAtVjI |  | 1
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | PULV A MOTOR WINDING TEMP-V1 | 3DP-TE733B | 1 | [7 empty] | 160°C (trip) | 0-180degC |  |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAoA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQiBNT1RPUiBXSU5ESU5HIFRFTVAtVjE
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | PULV A MOTOR WINDING TEMP-W1 | 3DP-TE735A | 1 | [5 empty] | 0 |  | 160°C (trip) | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAmw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQSBNT1RPUiBXSU5ESU5HIFRFTVAtVzE |  | 1
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | PULV A MOTOR WINDING TEMP-W2 | 3DP-TE736A | 1 | [5 empty] | 0 |  | 160°C (trip) | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAnA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQSBNT1RPUiBXSU5ESU5HIFRFTVAtVzI |  | 1
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | PULVERIZER A MOTOR BEARING TEMP-DE | 3DP-TE737A | 1 | [5 empty] | 0 |  | 95°C | 100°C (trip) | 0 |  | 60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA0g4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQSBNT1RPUiBCRUFSSU5HIFRFTVAtREU |  | 1
Boiler (BOL) | DP | 3DP-M731A | COAL PULVERIZER A MOTOR | PULVERIZER A MOTOR BEARING TEMP-NDE | 3DP-TE738A | 1 | [5 empty] | 0 |  | 95°C | 100°C (trip) | 0 |  | 60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA0w4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQSBNT1RPUiBCRUFSSU5HIFRFTVAtTkRF |  | 1
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | COAL PULV B MOT CUR | 3DP-BM731B-A | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA6QsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBCIE1PVCBDVVI |  | 1
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | PULVERIZER B SHAFT BRG TEMP | 3DP-TE705B | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA4A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQiBTSEFGVCBCUkcgVEVNUA
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | PULVERIZER B THRUST BRG TEMP | 3DP-TE706B | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA4Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQiBUSFJVU1QgQlJHIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | PULV B MOTOR WINDING TEMP-U1 | 3DP-TE731B | 1 | [5 empty] | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAng4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQiBNT1RPUiBXSU5ESU5HIFRFTVAtVTE |  | 1
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | PULV B MOTOR WINDING TEMP-U2 | 3DP-TE732B | 1 | [5 empty] | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAnw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQiBNT1RPUiBXSU5ESU5HIFRFTVAtVTI |  | 1
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | PULV B MOTOR WINDING TEMP-V1 | 3DP-TE733B | 1 | [5 empty] | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAoA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQiBNT1RPUiBXSU5ESU5HIFRFTVAtVjE
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | PULV B MOTOR WINDING TEMP-V1 | 3DP-TE733B | 1 | [5 empty] | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAoA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQiBNT1RPUiBXSU5ESU5HIFRFTVAtVjE |  | 1
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | PULV B MOTOR WINDING TEMP-V2 | 3DP-TE734B | 1 | [5 empty] | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAoQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQiBNT1RPUiBXSU5ESU5HIFRFTVAtVjI |  | 1
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | PULV B MOTOR WINDING TEMP-W1 | 3DP-TE735B | 1 | [5 empty] | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAog4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQiBNT1RPUiBXSU5ESU5HIFRFTVAtVzE |  | 1
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | PULV B MOTOR WINDING TEMP-W2 | 3DP-TE736B | 1 | [5 empty] | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAow4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQiBNT1RPUiBXSU5ESU5HIFRFTVAtVzI |  | 1
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | PULVERIZER B MOTOR BEARING TEMP-DE | 3DP-TE737B | 1 | [5 empty] | 0 |  | 95°C | 100°C (trip) | 0 |  | 60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA3g4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQiBNT1RPUiBCRUFSSU5HIFRFTVAtREU |  | 1
Boiler (BOL) | DP | 3DP-M731B | COAL PULVERIZER B MOTOR | PULVERIZER B MOTOR BEARING TEMP-NDE | 3DP-TE738B | 1 | [5 empty] | 0 |  | 95°C | 100°C (trip) | 0 |  | 60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA3w4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQiBNT1RPUiBCRUFSSU5HIFRFTVAtTkRF |  | 1
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | COAL PULV C MOT CUR | 3DP-BM731C-A | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA6gsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBDIE1PVCBDVVI |  | 1
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | PULVERIZER C SHAFT BRG TEMP | 3DP-TE705C | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA7A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBTSEFGVCBCUkcgVEVNUA
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | PULVERIZER C THRUST BRG TEMP | 3DP-TE706C | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA7Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBUSFJVU1QgQlJHIFRFTVA
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | PULV C MOTOR WINDING TEMP-U1 | 3DP-TE731C | 1 |  |  | 160°C |  |  | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pApQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQyBNT1RPUiBXSU5ESU5HIFRFTVAtVTE |  | 1
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | PULV C MOTOR WINDING TEMP-U2 | 3DP-TE732C | 1 |  |  | 160°C |  |  | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pApg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQyBNT1RPUiBXSU5ESU5HIFRFTVAtVTI |  | 1
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | PULV C MOTOR WINDING TEMP-V1 | 3DP-TE733C | 1 |  |  | 160°C |  |  | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pApw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQyBNT1RPUiBXSU5ESU5HIFRFTVAtVjE
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | PULV C MOTOR WINDING TEMP-V1 | 3DP-TE733C | 1 |  |  | 160°C |  |  | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pApw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQyBNT1RPUiBXSU5ESU5HIFRFTVAtVjE |  | 1
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | PULV C MOTOR WINDING TEMP-V2 | 3DP-TE734C | 1 |  |  | 160°C |  |  | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAqA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQyBNT1RPUiBXSU5ESU5HIFRFTVAtVjI |  | 1
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | PULV C MOTOR WINDING TEMP-W1 | 3DP-TE735C | 1 |  |  | 160°C |  |  | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAqQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQyBNT1RPUiBXSU5ESU5HIFRFTVAtVzE |  | 1
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | PULV C MOTOR WINDING TEMP-W2 | 3DP-TE736C | 1 |  |  | 160°C |  |  | 0 |  | 160°C | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAqg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQyBNT1RPUiBXSU5ESU5HIFRFTVAtVzI |  | 1
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | PULVERIZER C MOTOR BEARING TEMP-DE | 3DP-TE737C | 1 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA6g4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBNT1RPUiBCRUFSSU5HIFRFTVAtREU |  | 1
Boiler (BOL) | DP | 3DP-M731C | COAL PULVERIZER C MOTOR | PULVERIZER C MOTOR BEARING TEMP-NDE | 3DP-TE738C | 1 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA6w4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBNT1RPUiBCRUFSSU5HIFRFTVAtTkRF |  | 1
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | COAL PULV D MOT CUR | 3DP-BM731D-A | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA6wsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBEIE1PVCBDVVI |  | 1
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | PULVERIZER D SHAFT BRG TEMP | 3DP-TE705D | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA7A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBTSEFGVCBCUkcgVEVNUA
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | PULVERIZER D THRUST BRG TEMP | 3DP-TE706D | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA7Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBUSFJVU1QgQlJHIFRFTVA
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | PULV D MOTOR WINDING TEMP-U1 | 3DP-TE731D | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pArA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRCBNT1RPUiBXSU5ESU5HIFRFTVAtVTE |  | 1
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | PULV D MOTOR WINDING TEMP-U2 | 3DP-TE732D | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pArQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRCBNT1RPUiBXSU5ESU5HIFRFTVAtVTI |  | 1
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | PULV D MOTOR WINDING TEMP-V1 | 3DP-TE733D | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pArg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRCBNT1RPUiBXSU5ESU5HIFRFTVAtVjE
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | PULV D MOTOR WINDING TEMP-V1 | 3DP-TE733D | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pArg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRCBNT1RPUiBXSU5ESU5HIFRFTVAtVjE |  | 1
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | PULV D MOTOR WINDING TEMP-V2 | 3DP-TE734D | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pArw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRCBNT1RPUiBXSU5ESU5HIFRFTVAtVjI |  | 1
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | PULV D MOTOR WINDING TEMP-W1 | 3DP-TE735D | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAsA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRCBNT1RPUiBXSU5ESU5HIFRFTVAtVzE |  | 1
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | PULV D MOTOR WINDING TEMP-W2 | 3DP-TE736D | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAsQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRCBNT1RPUiBXSU5ESU5HIFRFTVAtVzI |  | 1
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | PULVERIZER D MOTOR BEARING TEMP-DE | 3DP-TE737D | 1 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA9g4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRCBNT1RPUiBCRUFSSU5HIFRFTVAtREU |  | 1
Boiler (BOL) | DP | 3DP-M731D | COAL PULVERIZER D MOTOR | PULVERIZER D MOTOR BEARING TEMP-NDE | 3DP-TE738D | 1 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA9w4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRCBNT1RPUiBCRUFSSU5HIFRFTVAtTkRF |  | 1
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | COAL PULV E MOT CUR | 3DP-BM731E-A | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA7AsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBFIE1PVCBDVVI |  | 1
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | PULVERIZER E SHAFT BRG TEMP | 3DP-TE705E | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA7A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBTSEFGVCBCUkcgVEVNUA
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | PULVERIZER E THRUST BRG TEMP | 3DP-TE706E | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA7Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBUSFJVU1QgQlJHIFRFTVA
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | PULV E MOTOR WINDING TEMP-U1 | 3DP-TE731E | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAsw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRSBNT1RPUiBXSU5ESU5HIFRFTVAtVTE |  | 1
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | PULV E MOTOR WINDING TEMP-U2 | 3DP-TE732E | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAtA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRSBNT1RPUiBXSU5ESU5HIFRFTVAtVTI |  | 1
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | PULV E MOTOR WINDING TEMP-V1 | 3DP-TE733E | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAtQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRSBNT1RPUiBXSU5ESU5HIFRFTVAtVjE
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | PULV E MOTOR WINDING TEMP-V1 | 3DP-TE733E | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAtQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRSBNT1RPUiBXSU5ESU5HIFRFTVAtVjE |  | 1
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | PULV E MOTOR WINDING TEMP-V2 | 3DP-TE734E | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAtg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRSBNT1RPUiBXSU5ESU5HIFRFTVAtVjI |  | 1
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | PULV E MOTOR WINDING TEMP-W1 | 3DP-TE735E | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAtw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRSBNT1RPUiBXSU5ESU5HIFRFTVAtVzE |  | 1
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | PULV E MOTOR WINDING TEMP-W2 | 3DP-TE736E | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAuA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRSBNT1RPUiBXSU5ESU5HIFRFTVAtVzI |  | 1
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | PULVERIZER E MOTOR BEARING TEMP-DE | 3DP-TE737E | 1 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAAg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRSBNT1RPUiBCRUFSSU5HIFRFTVAtREU |  | 1
Boiler (BOL) | DP | 3DP-M731E | COAL PULVERIZER E MOTOR | PULVERIZER E MOTOR BEARING TEMP-NDE | 3DP-TE738E | 1 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAAw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRSBNT1RPUiBCRUFSSU5HIFRFTVAtTkRF |  | 1
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | COAL PULV F MOT CUR | 3DP-BM731F-A | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA7QsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBGIE1PVCBDVVI |  | 1
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULVERIZER F SHAFT BRG TEMP | 3DP-TE705F | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA7A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBTSEFGVCBCUkcgVEVNUA
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULVERIZER F THRUST BRG TEMP | 3DP-TE706F | 1 |  |  |  | 70°C |  | 0 |  | 75°C | 85°C (trip) | 0 |  | <70°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA7Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBUSFJVU1QgQlJHIFRFTVA
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULV F MOTOR WINDING TEMP-U1 | 3DP-TE731F | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAug4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRiBNT1RPUiBXSU5ESU5HIFRFTVAtVTE
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULV F MOTOR WINDING TEMP-U2 | 3DP-TE732F | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAuw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRiBNT1RPUiBXSU5ESU5HIFRFTVAtVTI |  | 1
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULV F MOTOR WINDING TEMP-V1 | 3DP-TE733F | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAvA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRiBNT1RPUiBXSU5ESU5HIFRFTVAtVjE |  | 1
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULV F MOTOR WINDING TEMP-V1 | 3DP-TE733F | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAvA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRiBNT1RPUiBXSU5ESU5HIFRFTVAtVjE
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULV F MOTOR WINDING TEMP-V2 | 3DP-TE734F | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAvQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRiBNT1RPUiBXSU5ESU5HIFRFTVAtVjI |  | 1
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULV F MOTOR WINDING TEMP-W1 | 3DP-TE735F | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAvg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRiBNT1RPUiBXSU5ESU5HIFRFTVAtVzE |  | 1
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULV F MOTOR WINDING TEMP-W2 | 3DP-TE736F | 1 |  |  | 160°C |  |  | 0 |  | 999999 | 0-180degC | 0 |  | 85°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAvw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRiBNT1RPUiBXSU5ESU5HIFRFTVAtVzI |  | 1
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULVERIZER F MOTOR BEARING TEMP-DE | 3DP-TE737F | 0 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 0 | F1DPw1kUu10ziUaXEx2rIyo4pADg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBNT1RPUiBCRUFSSU5HIFRFTVAtREU |  | 1
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULVERIZER F MOTOR BEARING TEMP-NDE | 3DP-TE738F | 0 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 0 | F1DPw1kUu10ziUaXEx2rIyo4pADw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBNT1RPUiBCRUFSSU5HIFRFTVAtTkRF |  | 1
Boiler (BOL) | DP | 3DP-M761A | COAL PULVERIZER A LUBRICATING OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-M761B | COAL PULVERIZER B LUBRICATING OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-M761C | COAL PULVERIZER C LUBRICATING OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-M761D | COAL PULVERIZER D LUBRICATING OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-M761E | COAL PULVERIZER E LUBRICATING OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-M761F | COAL PULVERIZER F LUBRICATING OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-M781A | COAL PULVERIZER A HYDRAULIC OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-M781B | COAL PULVERIZER B HYDRAULIC OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-M781C | COAL PULVERIZER C HYDRAULIC OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-M781D | COAL PULVERIZER D HYDRAULIC OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-M781E | COAL PULVERIZER E HYDRAULIC OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-M781F | COAL PULVERIZER F HYDRAULIC OIL PUMP MOTOR
Boiler (BOL) | DP | 3DP-P761A | COAL PULVERIZER A LUBRICATING OIL PUMP | PULVERIZER-A LUB OIL PRESS. | 3DP-PX702A | 1 |  |  |  | 0.8 barg | 0.6 barg |  |  |  | 0-10barg |  |  | >2 barg |  | F1DPw1kUu10ziUaXEx2rIyo4pA0A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQSBMVUIgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-P761B | COAL PULVERIZER B LUBRICATING OIL PUMP | PULVERIZER-B LUB OIL PRESS. | 3DP-PX702B | 1 |  |  |  | 0.8 barg | 0.6 barg |  |  |  | 0-10barg |  |  | >2 barg |  | F1DPw1kUu10ziUaXEx2rIyo4pA3A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQiBMVUIgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-P761C | COAL PULVERIZER C LUBRICATING OIL PUMP | PULVERIZER-C LUB OIL PRESS. | 3DP-PX702C | 1 |  |  |  | 0.8 barg | 0.6 barg |  |  |  | 0-10barg |  |  | >2 barg |  | F1DPw1kUu10ziUaXEx2rIyo4pA6A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBMVUIgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-P761D | COAL PULVERIZER D LUBRICATING OIL PUMP | PULVERIZER-D LUB OIL PRESS. | 3DP-PX702D | 1 |  |  |  | 0.8 barg | 0.6 barg |  |  |  | 0-10barg |  |  | >2 barg |  | F1DPw1kUu10ziUaXEx2rIyo4pA9A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRCBMVUIgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-P761E | COAL PULVERIZER E LUBRICATING OIL PUMP | PULVERIZER-E LUB OIL PRESS. | 3DP-PX702E | 1 |  |  |  | 0.8 barg | 0.6 barg |  |  |  | 0-10barg |  |  | >2 barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAAA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRSBMVUIgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-P761F | COAL PULVERIZER F LUBRICATING OIL PUMP | PULVERIZER-F LUB OIL PRESS. | 3DP-PX702F | 1 |  |  |  | 0.8 barg | 0.6 barg |  |  |  | 0-10barg |  |  | >2 barg |  | F1DPw1kUu10ziUaXEx2rIyo4pADA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBMVUIgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-P761A | COAL PULVERIZER A LUBRICATING OIL PUMP | PULVERIZER-A LUB OIL TEMP. | 3DP-TE704A | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA0Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQSBMVUIgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P761B | COAL PULVERIZER B LUBRICATING OIL PUMP | PULVERIZER-B LUB OIL TEMP. | 3DP-TE704B | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA3Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQiBMVUIgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P761C | COAL PULVERIZER C LUBRICATING OIL PUMP | PULVERIZER-C LUB OIL TEMP. | 3DP-TE704C | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA6Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBMVUIgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P761D | COAL PULVERIZER D LUBRICATING OIL PUMP | PULVERIZER-D LUB OIL TEMP. | 3DP-TE704D | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA9Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRCBMVUIgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P761E | COAL PULVERIZER E LUBRICATING OIL PUMP | PULVERIZER-E LUB OIL TEMP. | 3DP-TE704E | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAAQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRSBMVUIgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P761F | COAL PULVERIZER F LUBRICATING OIL PUMP | PULVERIZER-F LUB OIL TEMP. | 3DP-TE704F | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pADQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBMVUIgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P761A | COAL PULVERIZER A LUBRICATING OIL PUMP | PULV A LUB OIL GEAR HOUSING OIL TEMP | 3DP-TE703A | 1 |  |  |  | 60°C |  | 0 |  | 70°C | 80°C (trip) | 0 |  | <60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAlg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQSBMVUIgT0lMIEdFQVIgSE9VU0lORyBPSUwgVEVNUA
Boiler (BOL) | DP | 3DP-P761B | COAL PULVERIZER B LUBRICATING OIL PUMP | PULV A LUB OIL GEAR HOUSING OIL TEMP | 3DP-TE703B | 1 |  |  |  | 60°C |  | 0 |  | 70°C | 80°C (trip) | 0 |  | <60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAnQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQiBMVUIgT0lMIEdFQVIgSE9VU0lORyBPSUwgVEVNUA
Boiler (BOL) | DP | 3DP-P761C | COAL PULVERIZER C LUBRICATING OIL PUMP | PULV A LUB OIL GEAR HOUSING OIL TEMP | 3DP-TE703C | 1 |  |  |  | 60°C |  | 0 |  | 70°C | 80°C (trip) | 0 |  | <60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pApA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgQyBMVUIgT0lMIEdFQVIgSE9VU0lORyBPSUwgVEVNUA
Boiler (BOL) | DP | 3DP-P761D | COAL PULVERIZER D LUBRICATING OIL PUMP | PULV A LUB OIL GEAR HOUSING OIL TEMP | 3DP-TE703D | 1 |  |  |  | 60°C |  | 0 |  | 70°C | 80°C (trip) | 0 |  | <60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAqw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRCBMVUIgT0lMIEdFQVIgSE9VU0lORyBPSUwgVEVNUA
Boiler (BOL) | DP | 3DP-P761E | COAL PULVERIZER E LUBRICATING OIL PUMP | PULV A LUB OIL GEAR HOUSING OIL TEMP | 3DP-TE703E | 1 |  |  |  | 60°C |  | 0 |  | 70°C | 80°C (trip) | 0 |  | <60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAsg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRSBMVUIgT0lMIEdFQVIgSE9VU0lORyBPSUwgVEVNUA
Boiler (BOL) | DP | 3DP-P761F | COAL PULVERIZER F LUBRICATING OIL PUMP | PULV A LUB OIL GEAR HOUSING OIL TEMP | 3DP-TE703F | 1 |  |  |  | 60°C |  | 0 |  | 70°C | 80°C (trip) | 0 |  | <60°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAuQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgRiBMVUIgT0lMIEdFQVIgSE9VU0lORyBPSUwgVEVNUA
Boiler (BOL) | DP | 3DP-P761A | COAL PULVERIZER A LUBRICATING OIL PUMP | PULVERIZER-A LUB OIL COOLER INLET OIL TEMP. | 3DP-TG702A | [12 empty] | 60°C |  | 0
Boiler (BOL) | DP | 3DP-P761B | COAL PULVERIZER B LUBRICATING OIL PUMP | PULVERIZER-B LUB OIL COOLER INLET OIL TEMP. | 3DP-TG702B | [12 empty] | 60°C |  | 0
Boiler (BOL) | DP | 3DP-P761C | COAL PULVERIZER C LUBRICATING OIL PUMP | PULVERIZER-C LUB OIL COOLER INLET OIL TEMP. | 3DP-TG702C | [12 empty] | 60°C |  | 0
Boiler (BOL) | DP | 3DP-P761D | COAL PULVERIZER D LUBRICATING OIL PUMP | PULVERIZER-D LUB OIL COOLER INLET OIL TEMP. | 3DP-TG702D | [12 empty] | 60°C |  | 0
Boiler (BOL) | DP | 3DP-P761E | COAL PULVERIZER E LUBRICATING OIL PUMP | PULVERIZER-E LUB OIL COOLER INLET OIL TEMP. | 3DP-TG702E | [12 empty] | 60°C |  | 0
Boiler (BOL) | DP | 3DP-P761F | COAL PULVERIZER F LUBRICATING OIL PUMP | PULVERIZER-F LUB OIL COOLER INLET OIL TEMP. | 3DP-TG702F | [12 empty] | 60°C |  | 0
Boiler (BOL) | DP | 3DP-P761A | COAL PULVERIZER A LUBRICATING OIL PUMP | PULVERIZER-A LUB OIL COOLER OUTLET OIL TEMP. | 3DP-TG703A | [12 empty] | 50°C |  | 0
Boiler (BOL) | DP | 3DP-P761B | COAL PULVERIZER B LUBRICATING OIL PUMP | PULVERIZER-B LUB OIL COOLER OUTLET OIL TEMP. | 3DP-TG703B | [12 empty] | 50°C |  | 0
Boiler (BOL) | DP | 3DP-P761C | COAL PULVERIZER C LUBRICATING OIL PUMP | PULVERIZER-C LUB OIL COOLER OUTLET OIL TEMP. | 3DP-TG703C | [12 empty] | 50°C |  | 0
Boiler (BOL) | DP | 3DP-P761D | COAL PULVERIZER D LUBRICATING OIL PUMP | PULVERIZER-D LUB OIL COOLER OUTLET OIL TEMP. | 3DP-TG703D | [12 empty] | 50°C |  | 0
Boiler (BOL) | DP | 3DP-P761E | COAL PULVERIZER E LUBRICATING OIL PUMP | PULVERIZER-E LUB OIL COOLER OUTLET OIL TEMP. | 3DP-TG703E | [12 empty] | 50°C |  | 0
Boiler (BOL) | DP | 3DP-P761F | COAL PULVERIZER F LUBRICATING OIL PUMP | PULVERIZER-F LUB OIL COOLER OUTLET OIL TEMP. | 3DP-TG703F | [12 empty] | 50°C |  | 0
Boiler (BOL) | DP | 3DP-P781A | COAL PULVERIZER A HYDRAULIC OIL PUMP | PULVERIZER-A HYDRO POWER OIL PUMP DISCHARGE PRESS. | 3DP-PG701A | [14 empty] | 0
Boiler (BOL) | DP | 3DP-P781B | COAL PULVERIZER B HYDRAULIC OIL PUMP | PULVERIZER-B HYDRO POWER OIL PUMP DISCGARGE PRESS. | 3DP-PG701B | [14 empty] | 0
Boiler (BOL) | DP | 3DP-P781C | COAL PULVERIZER C HYDRAULIC OIL PUMP | PULVERIZER-C HYDRO POWER OIL PUMP DISCGARGE PRESS. | 3DP-PG701C | [14 empty] | 0
Boiler (BOL) | DP | 3DP-P781D | COAL PULVERIZER D HYDRAULIC OIL PUMP | PULVERIZER-D HYDRO POWER OIL PUMP DISCGARGE PRESS. | 3DP-PG701D | [14 empty] | 0
Boiler (BOL) | DP | 3DP-P781E | COAL PULVERIZER E HYDRAULIC OIL PUMP | PULVERIZER-E HYDRO POWER OIL PUMP DISCGARGE PRESS. | 3DP-PG701E | [14 empty] | 0
Boiler (BOL) | DP | 3DP-P781F | COAL PULVERIZER F HYDRAULIC OIL PUMP | PULVERIZER-F HYDRO POWER OIL PUMP DISCGARGE PRESS. | 3DP-PG701F | [14 empty] | 0
Boiler (BOL) | DP | 3DP-P781A | COAL PULVERIZER A HYDRAULIC OIL PUMP | PULVERIZER-A HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TG701A | 1 | [7 empty] | tidak bisa didisplay di DCS |  |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAzQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQSBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781B | COAL PULVERIZER B HYDRAULIC OIL PUMP | PULVERIZER-B HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TG701B | 1 | [7 empty] | tidak bisa didisplay di DCS |  |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pA2Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQiBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781C | COAL PULVERIZER C HYDRAULIC OIL PUMP | PULVERIZER-C HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TG701C | 1 | [7 empty] | tidak bisa didisplay di DCS |  |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pA5Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781D | COAL PULVERIZER D HYDRAULIC OIL PUMP | PULVERIZER-D HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TG701D | 1 | [7 empty] | tidak bisa didisplay di DCS |  |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pA8Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRCBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781E | COAL PULVERIZER E HYDRAULIC OIL PUMP | PULVERIZER-E HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TG701E | 1 | [7 empty] | tidak bisa didisplay di DCS |  |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pA_Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRSBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781F | COAL PULVERIZER F HYDRAULIC OIL PUMP | PULVERIZER-F HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TG701F | 1 | [7 empty] | tidak bisa didisplay di DCS |  |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pACQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781A | COAL PULVERIZER A HYDRAULIC OIL PUMP | PULVERIZER-A HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TE702A | 1 |  |  |  | 40°C |  |  |  | 60°C | 0-150degC |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAzQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQSBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781B | COAL PULVERIZER B HYDRAULIC OIL PUMP | PULVERIZER-B HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TE702B | 1 |  |  |  | 40°C |  |  |  | 60°C | 0-150degC |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pA2Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQiBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781C | COAL PULVERIZER C HYDRAULIC OIL PUMP | PULVERIZER-C HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TE702C | 1 |  |  |  | 40°C |  |  |  | 60°C | 0-150degC |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pA5Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781D | COAL PULVERIZER D HYDRAULIC OIL PUMP | PULVERIZER-D HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TE702D | 1 |  |  |  | 40°C |  |  |  | 60°C | 0-150degC |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pA8Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRCBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781E | COAL PULVERIZER E HYDRAULIC OIL PUMP | PULVERIZER-E HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TE702E | 1 |  |  |  | 40°C |  |  |  | 60°C | 0-150degC |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pA_Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRSBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781F | COAL PULVERIZER F HYDRAULIC OIL PUMP | PULVERIZER-F HYDRAULIC OIL UNIT OIL TEMP. | 3DP-TE702F | 1 |  |  |  | 40°C |  |  |  | 60°C | 0-150degC |  |  | 40°C |  | F1DPw1kUu10ziUaXEx2rIyo4pACQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBIWURSQVVMSUMgT0lMIFVOSVQgT0lMIFRFTVA |  | 1
Boiler (BOL) | DP | 3DP-P781A | COAL PULVERIZER A HYDRAULIC OIL PUMP | PULVERIZER-A HYDRAULIC OIL PRESS. | 3DP-PX701A | 1 |  |  | 33 |  |  | 0 |  | 115 | 0-140barg | 0 |  | Now:93 |  | F1DPw1kUu10ziUaXEx2rIyo4pAzA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQSBIWURSQVVMSUMgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-P781B | COAL PULVERIZER B HYDRAULIC OIL PUMP | PULVERIZER-B HYDRAULIC OIL PRESS. | 3DP-PX701B | 1 |  |  | 33 |  |  | 0 |  | 115 | 0-140barg | 0 |  | now:1, alarm low |  | F1DPw1kUu10ziUaXEx2rIyo4pA2A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQiBIWURSQVVMSUMgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-P781C | COAL PULVERIZER C HYDRAULIC OIL PUMP | PULVERIZER-C HYDRAULIC OIL PRESS. | 3DP-PX701C | 1 |  |  | 33 |  |  | 0 |  | 115 | 0-140barg | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA5A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBIWURSQVVMSUMgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-P781D | COAL PULVERIZER D HYDRAULIC OIL PUMP | PULVERIZER-D HYDRAULIC OIL PRESS. | 3DP-PX701D | 1 |  |  | 33 |  |  | 0 |  | 115 | 0-140barg | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA8A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRCBIWURSQVVMSUMgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-P781E | COAL PULVERIZER E HYDRAULIC OIL PUMP | PULVERIZER-E HYDRAULIC OIL PRESS. | 3DP-PX701E | 1 |  |  | 33 |  |  | 0 |  | 115 | 0-140barg | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA_A4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRSBIWURSQVVMSUMgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-P781F | COAL PULVERIZER F HYDRAULIC OIL PUMP | PULVERIZER-F HYDRAULIC OIL PRESS. | 3DP-PX701F | 1 |  |  | 33 |  |  | 0 |  | 115 | 0-140barg | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pACA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBIWURSQVVMSUMgT0lMIFBSRVNT |  | 1
Boiler (BOL) | DP | 3DP-BM731A | PULVERIZER A | PULVERIZER-A OUTLET TEMP. | 3DP-TE701A | 1 |  |  | 55°C |  |  | 0 |  | 100°C (trip) |  | 0 |  | 65°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAFA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItQSBPVVRMRVQgVEVNUA
Boiler (BOL) | DP | 3DP-BM731B | PULVERIZER B | PULVERIZER-B OUTLET TEMP. | 3DP-TE701B | 1 |  |  | 55°C |  |  | 0 |  | 100°C (trip) |  | 0 |  | 65°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAGA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItQiBPVVRMRVQgVEVNUA
Boiler (BOL) | DP | 3DP-BM731C | PULVERIZER C | PULVERIZER-C OUTLET TEMP. | 3DP-TE701C | 1 |  |  | 55°C |  |  | 0 |  | 100°C (trip) |  | 0 |  | 65°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAHA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItQyBPVVRMRVQgVEVNUA
Boiler (BOL) | DP | 3DP-BM731D | PULVERIZER D | PULVERIZER-D OUTLET TEMP. | 3DP-TE701D | 1 |  |  | 55°C |  |  | 0 |  | 100°C (trip) |  | 0 |  | 65°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAIA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItRCBPVVRMRVQgVEVNUA
Boiler (BOL) | DP | 3DP-BM731E | PULVERIZER E | PULVERIZER-E OUTLET TEMP. | 3DP-TE701E | 1 |  |  | 55°C |  |  | 0 |  | 100°C (trip) |  | 0 |  | 65°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAJA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItRSBPVVRMRVQgVEVNUA
Boiler (BOL) | DP | 3DP-BM731F | PULVERIZER F | PULVERIZER-F OUTLET TEMP. | 3DP-TE701F | 1 |  |  | 55°C |  |  | 0 |  | 100°C (trip) |  | 0 |  | 65°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAKA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItRiBPVVRMRVQgVEVNUA
Boiler (BOL) | DP | 3DP-BM731A | PULVERIZER A | ROLL LIFT | 3DP-CVT711A | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAFQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItQSBST0xMIExJRlQ
Boiler (BOL) | DP | 3DP-BM731B | PULVERIZER B | ROLL LIFT | 3DP-CVT711B | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAGQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItQiBST0xMIExJRlQ
Boiler (BOL) | DP | 3DP-BM731C | PULVERIZER C | ROLL LIFT | 3DP-CVT711C | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAHQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItQyBST0xMIExJRlQ
Boiler (BOL) | DP | 3DP-BM731D | PULVERIZER D | ROLL LIFT | 3DP-CVT711D | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAIQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItRCBST0xMIExJRlQ
Boiler (BOL) | DP | 3DP-BM731E | PULVERIZER E | ROLL LIFT | 3DP-CVT711E | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAJQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItRSBST0xMIExJRlQ
Boiler (BOL) | DP | 3DP-BM731F | PULVERIZER F | ROLL LIFT | 3DP-CVT711F | 1 |  |  | -999999 |  |  | 0 |  | 220 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAKQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItRiBST0xMIExJRlQ
Boiler (BOL) | DP | 3DP-BM731A | PULVERIZER A | PULVERIZER MRS CUR | 3DP-HSIG001 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-150A | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA6AsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBBIE1PVCBDVVI
Boiler (BOL) | DP | 3DP-BM731B | PULVERIZER B | PULVERIZER MRS CUR | 3DP-HSIG003 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-150A | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA6QsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBCIE1PVCBDVVI
Boiler (BOL) | DP | 3DP-BM731C | PULVERIZER C | PULVERIZER MRS CUR | 3DP-HSIG005 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-150A | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA6gsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBDIE1PVCBDVVI
Boiler (BOL) | DP | 3DP-BM731D | PULVERIZER D | PULVERIZER MRS CUR | 3DP-HSIG007 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-150A | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA6wsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBEIE1PVCBDVVI
Boiler (BOL) | DP | 3DP-BM731E | PULVERIZER E | PULVERIZER MRS CUR | 3DP-HSIG009 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-150A | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA7AsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBFIE1PVCBDVVI
Boiler (BOL) | DP | 3DP-BM731F | PULVERIZER F | PULVERIZER MRS CUR | 3DP-HSIG011 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-150A | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA7QsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNPQUwgUFVMViBGIE1PVCBDVVI
Boiler (BOL) | DP | 3DP-BM731A | PULVERIZER A | PULVERIZER MRS SPEED | 3DP-HSIG002 | [14 empty] | 0
Boiler (BOL) | DP | 3DP-BM731B | PULVERIZER B | PULVERIZER MRS SPEED | 3DP-HSIG004 | [14 empty] | 0
Boiler (BOL) | DP | 3DP-BM731C | PULVERIZER C | PULVERIZER MRS SPEED | 3DP-HSIG006 | [14 empty] | 0
Boiler (BOL) | DP | 3DP-BM731D | PULVERIZER D | PULVERIZER MRS SPEED | 3DP-HSIG008 | [14 empty] | 0
Boiler (BOL) | DP | 3DP-BM731E | PULVERIZER E | PULVERIZER MRS SPEED | 3DP-HSIG010 | [14 empty] | 0
Boiler (BOL) | DP | 3DP-BM731F | PULVERIZER F | PULVERIZER MRS SPEED | 3DP-HSIG012 | [14 empty] | 0
Boiler (BOL) | DP | 3DP-BM731A | PULVERIZER A | PULVERIZER VIBRATION | 3DP-VE701A | 1 | [5 empty] | 0 |  | 150µm |  | 0 |  | >80µm |  | F1DPw1kUu10ziUaXEx2rIyo4pAFg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItQSBWSUJSQVRJT04
Boiler (BOL) | DP | 3DP-BM731B | PULVERIZER B | PULVERIZER VIBRATION | 3DP-VE701B | 1 | [5 empty] | 0 |  | 150µm |  | 0 |  | >80µm |  | F1DPw1kUu10ziUaXEx2rIyo4pAGg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItQiBWSUJSQVRJT04
Boiler (BOL) | DP | 3DP-BM731C | PULVERIZER C | PULVERIZER VIBRATION | 3DP-VE701C | 1 | [5 empty] | 0 |  | 150µm |  | 0 |  | >80µm |  | F1DPw1kUu10ziUaXEx2rIyo4pAHg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItQyBWSUJSQVRJT04
Boiler (BOL) | DP | 3DP-BM731D | PULVERIZER D | PULVERIZER VIBRATION | 3DP-VE701D | 1 | [5 empty] | 0 |  | 150µm |  | 0 |  | >80µm |  | F1DPw1kUu10ziUaXEx2rIyo4pAIg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItRCBWSUJSQVRJT04
Boiler (BOL) | DP | 3DP-BM731E | PULVERIZER E | PULVERIZER VIBRATION | 3DP-VE701E | 1 | [5 empty] | 0 |  | 150µm |  | 0 |  | >80µm |  | F1DPw1kUu10ziUaXEx2rIyo4pAJg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItRSBWSUJSQVRJT04
Boiler (BOL) | DP | 3DP-BM731F | PULVERIZER F | PULVERIZER VIBRATION | 3DP-VE701F | 1 | [5 empty] | 0 |  | 150µm |  | 0 |  | >80µm |  | F1DPw1kUu10ziUaXEx2rIyo4pAKg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVItRiBWSUJSQVRJT04
Boiler (BOL) | DP | 3DP-BM731A | PULVERIZER A | PULVERIZER INERTING STEAM FLOW | 3DPIN-FIX701 |  |  |  | 0.5 |  |  | 0 |  | 999999 |  | 0 |  |  |  | 0
Boiler (BOL) | DP | 3DP-BM731B | PULVERIZER B | PULVERIZER INERTING STEAM FLOW | 3DPIN-FIX701 | [14 empty] | 0
Boiler (BOL) | DP | 3DP-BM731C | PULVERIZER C | PULVERIZER INERTING STEAM FLOW | 3DPIN-FIX701 | [14 empty] | 0
Boiler (BOL) | DP | 3DP-BM731D | PULVERIZER D | PULVERIZER INERTING STEAM FLOW | 3DPIN-FIX701 | [14 empty] | 0
Boiler (BOL) | DP | 3DP-BM731E | PULVERIZER E | PULVERIZER INERTING STEAM FLOW | 3DPIN-FIX701 | [14 empty] | 0
Boiler (BOL) | DP | 3DP-BM731F | PULVERIZER F | PULVERIZER INERTING STEAM FLOW | 3DPIN-FIX701 | [14 empty] | 0
Boiler (BOL) | DP | 3DP-BM731A | PULVERIZER A | PULV INERTING STEAM PRESS | 3DPIN-PIX501 | 1 |  |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAwQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgSU5FUlRJTkcgU1RFQU0gUFJFU1M
Boiler (BOL) | DP | 3DP-BM731B | PULVERIZER B | PULV INERTING STEAM PRESS | 3DPIN-PIX501 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgSU5FUlRJTkcgU1RFQU0gUFJFU1M
Boiler (BOL) | DP | 3DP-BM731C | PULVERIZER C | PULV INERTING STEAM PRESS | 3DPIN-PIX501 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgSU5FUlRJTkcgU1RFQU0gUFJFU1M
Boiler (BOL) | DP | 3DP-BM731D | PULVERIZER D | PULV INERTING STEAM PRESS | 3DPIN-PIX501 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgSU5FUlRJTkcgU1RFQU0gUFJFU1M
Boiler (BOL) | DP | 3DP-BM731E | PULVERIZER E | PULV INERTING STEAM PRESS | 3DPIN-PIX501 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgSU5FUlRJTkcgU1RFQU0gUFJFU1M
Boiler (BOL) | DP | 3DP-BM731F | PULVERIZER F | PULV INERTING STEAM PRESS | 3DPIN-PIX501 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFYgSU5FUlRJTkcgU1RFQU0gUFJFU1M
Boiler (BOL) | DP | 3DP-BM731A | PULVERIZER A | PULVERIZER INERTING STEAM TEMP | 3DPIN-TE501 | 1 |  |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAEg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgSU5FUlRJTkcgU1RFQU0gVEVNUA
Boiler (BOL) | DP | 3DP-BM731B | PULVERIZER B | PULVERIZER INERTING STEAM TEMP | 3DPIN-TE501 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAEg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgSU5FUlRJTkcgU1RFQU0gVEVNUA
Boiler (BOL) | DP | 3DP-BM731C | PULVERIZER C | PULVERIZER INERTING STEAM TEMP | 3DPIN-TE501 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAEg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgSU5FUlRJTkcgU1RFQU0gVEVNUA
Boiler (BOL) | DP | 3DP-BM731D | PULVERIZER D | PULVERIZER INERTING STEAM TEMP | 3DPIN-TE501 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAEg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgSU5FUlRJTkcgU1RFQU0gVEVNUA
Boiler (BOL) | DP | 3DP-BM731E | PULVERIZER E | PULVERIZER INERTING STEAM TEMP | 3DPIN-TE501 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAEg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgSU5FUlRJTkcgU1RFQU0gVEVNUA
Boiler (BOL) | DP | 3DP-BM731F | PULVERIZER F | PULVERIZER INERTING STEAM TEMP | 3DPIN-TE501 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAEg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgSU5FUlRJTkcgU1RFQU0gVEVNUA
FGD Support (SUP) | DS | 00DS-M851 | GYPSUM HYDROCLONE OVERFLOW TANK AGITATOR MOTOR
FGD Support (SUP) | DS | 00DS-M860A | GYPSUM HYDROCLONE OVERFLOW TANK PUMP A MOTOR | GYP HDCLN A TOP PRESS | 00DS-PIX851A | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-M860B | GYPSUM HYDROCLONE OVERFLOW TANK PUMP B MOTOR | GYP HDCLN B TOP PRESS | 00DS-PIX851B | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-M883A | CHLORIDE PURGE TANK PUMP A MOTOR
FGD Support (SUP) | DS | 00DS-M883B | CHLORIDE PURGE TANK PUMP B MOTOR
FGD Support (SUP) | DS | 00DS-M888 | CHLORIDE PURGE TANK AGITATOR MOTOR
FGD Support (SUP) | DS | 00DS-M900 | VACUUM BELT FILTER A MOTOR
FGD Support (SUP) | DS | 00DS-M901 | VACUUM BELT FILTER A VACUUM PUMP MOTOR
FGD Support (SUP) | DS | 00DS-M902A | VACUUM BELT FILTER A WASH TANK PUMP A MOTOR
FGD Support (SUP) | DS | 00DS-M902B | VACUUM BELT FILTER A/ WASH TANK PUMP B MOTOR
FGD Support (SUP) | DS | 00DS-M935 | VACUUM BELT FILTER B MOTOR
FGD Support (SUP) | DS | 00DS-M936 | VACUUM BELT FILTER B VACUUM PUMP MOTOR
FGD Support (SUP) | DS | 00DS-M937A | VACUUM BELT FILTER B WASH TANK PUMP A MOTOR
FGD Support (SUP) | DS | 00DS-M937B | VACUUM BELT FILTER B WASH TANK PUMP B MOTOR
FGD Support (SUP) | DS | 00DS-M975 | RECLAIM WATER TANK AGITATOR MOTOR
FGD Support (SUP) | DS | 00DS-M978A | RECLAIM WATER TANK PUMP A MOTOR
FGD Support (SUP) | DS | 00DS-M978B | RECLAIM WATER TANK PUMP B MOTOR
FGD Support (SUP) | DS | 00DS-P860A | GYPSUM HYDROCLONE OVERFLOW TANK PUMP A | GYP HDCLN OVFL TK PMP A OUTL PRESS | 00DS-PG860A | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-P860B | GYPSUM HYDROCLONE OVERFLOW TANK PUMP B | GYP HDCLN OVFL TK PMP B OUTL PRESS | 00DS-PG860B | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-P883A | CHLORIDE PURGE TANK PUMP A | CLR PGR TK PMP A OUTL PRESS | 00DS-PG883A | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-P883B | CHLORIDE PURGE TANK PUMP B | CLR PGR TK PMP B OUTL PRESS | 00DS-PG883B | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-P901 | VACUUM BELT FILTER A VACUUM PUMP | VAC BFR A VAC PMP INL PRESS | 00DS-PG901 | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-P936 | VACUUM BELT FILTER B VACUUM PUMP | VAC BFR B VAC PMP INL PRESS | 00DS-PG936 | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-P902A | VACUUM BELT FILTER A WASH PUMP A | VAC BFR A WASH PMP A OUTL PRESS | 00DS-PG902A | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-P902B | VACUUM BELT FILTER A WASH PUMP B | VAC BFR A WASH PMP B OUTL PRESS | 00DS-PG902B | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-P937A | VACUUM BELT FILTER B WASH PUMP A | VAC BFR B WASH PMP A OUTL PRESS | 00DS-PG937A | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-P937B | VACUUM BELT FILTER B WASH PUMP B | VAC BFR B WASH PMP B OUTL PRESS | 00DS-PG937B | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-P978A | RECLAIM WATER TANK PUMP A | RCLM WTR TK PMP A OUTL PRESS | 00DS-PG978A | [14 empty] | 0
FGD Support (SUP) | DS | 00DS-P978B | RECLAIM WATER TANK PUMP B | RCLM WTR TK PMP B OUTL PRESS | 00DS-PG978B | [14 empty] | 0
Sis Pemakaian Sendiri (SPS) | EHS | 3EG-E001 | EMERGENCY DIESEL ENGINE GENERATOR | EHC OIL PMP A OUTL FR DP | 3EHS-DPIX001A | 1 |  |  | -999999 |  |  | 0 |  | 5 | 0-7bar | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAlAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkVIQyBPSUwgUE1QIEEgT1VUTCBGUiBEUA
Sis Pemakaian Sendiri (SPS) | EHS | 3EG-E001 | EMERGENCY DIESEL ENGINE GENERATOR | EHC OIL PMP B OUTL FR DP | 3EHS-DPIX001B | 1 |  |  | -999999 |  |  | 0 |  | 5 | 0-7bar | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAlQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkVIQyBPSUwgUE1QIEIgT1VUTCBGUiBEUA
Sis Pemakaian Sendiri (SPS) | EHS | 3EG-E001 | EMERGENCY DIESEL ENGINE GENERATOR | EHC OIL RTN FR DP | 3EHS-DPIX002 | 1 |  |  | -999999 |  |  | 0 |  | 2025-05-01 | 0-4bar | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAlwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkVIQyBPSUwgUlROIEZSIERQ
Sis Pemakaian Sendiri (SPS) | EHS | 3EG-E001 | EMERGENCY DIESEL ENGINE GENERATOR | EHC OIL PRESS | 3EHS-PIX001 | 1 |  |  | 135 |  |  | 0 |  | 999999 | 0-250 barg | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAlgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkVIQyBPSUwgUFJFU1M
Sis Pemakaian Sendiri (SPS) | EHS | 3EG-E001 | EMERGENCY DIESEL ENGINE GENERATOR | EHC OIL TK OIL TEMP | 3EHS-TE001 | 1 |  |  | 12 |  |  | 0 |  | 65 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkVIQyBPSUwgVEsgT0lMIFRFTVA
Air Flue Gas (AFG) | ESP | 3ESP-RD801 | ESP A CHAMBER 1 FIELD 1 - COLLECTING RAPPING MOTOR | ESP A CHBR 1 FLD 1 - HPR A TEMP | 3ESP-TE863A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD801 | ESP A CHAMBER 1 FIELD 1 - COLLECTING RAPPING MOTOR | ESP A CHBR 1 FLD 1 - HPR B TEMP | 3ESP-TE863B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD802 | ESP A CHAMBER 2 FIELD 1 - COLLECTING RAPPING MOTOR | ESP A CHBR 2 FLD 1 - HPR A TEMP | 3ESP-TE864A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD802 | ESP A CHAMBER 2 FIELD 1 - COLLECTING RAPPING MOTOR | ESP A CHBR 2 FLD 1 - HPR B TEMP | 3ESP-TE864B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD803 | ESP B CHAMBER 1 FIELD 1 - COLLECTING RAPPING MOTOR | ESP B CHBR 1 FLD 1 - HPR A TEMP | 3ESP-TE865A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD803 | ESP B CHAMBER 1 FIELD 1 - COLLECTING RAPPING MOTOR | ESP B CHBR 1 FLD 1 - HPR A TEMP | 3ESP-TE865B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD804 | ESP B CHAMBER 2 FIELD 1 - COLLECTING RAPPING MOTOR | ESP B CHBR 2 FLD 1 - HPR A TEMP | 3ESP-TE866A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD804 | ESP B CHAMBER 2 FIELD 1 - COLLECTING RAPPING MOTOR | ESP B CHBR 2 FLD 1 - HPR A TEMP | 3ESP-TE866B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD805 | ESP A CHAMBER 1 FIELD 2 - COLLECTING RAPPING MOTOR | ESP A CHBR 1 FLD 2 - HPR A TEMP | 3ESP-TE867A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD805 | ESP A CHAMBER 1 FIELD 2 - COLLECTING RAPPING MOTOR | ESP A CHBR 1 FLD 2 - HPR A TEMP | 3ESP-TE867B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD806 | ESP A CHAMBER 2 FIELD 2 - COLLECTING RAPPING MOTOR | ESP A CHBR 2 FLD 2 - HPR A TEMP | 3ESP-TE868A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD806 | ESP A CHAMBER 2 FIELD 2 - COLLECTING RAPPING MOTOR | ESP A CHBR 2 FLD 2 - HPR A TEMP | 3ESP-TE868B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD807 | ESP B CHAMBER 1 FIELD 2 - COLLECTING RAPPING MOTOR | ESP B CHBR 1 FLD 2 - HPR A TEMP | 3ESP-TE869A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD807 | ESP B CHAMBER 1 FIELD 2 - COLLECTING RAPPING MOTOR | ESP B CHBR 1 FLD 2 - HPR A TEMP | 3ESP-TE869B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD808 | ESP B CHAMBER 2 FIELD 2 - COLLECTING RAPPING MOTOR | ESP B CHBR 2 FLD 2 - HPR A TEMP | 3ESP-TE870A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD808 | ESP B CHAMBER 2 FIELD 2 - COLLECTING RAPPING MOTOR | ESP B CHBR 2 FLD 2 - HPR A TEMP | 3ESP-TE870B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD809 | ESP A CHAMBER 1 FIELD 3 - COLLECTING RAPPING MOTOR | ESP A CHBR 1 FLD 3 - HPR A TEMP | 3ESP-TE871A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD809 | ESP A CHAMBER 1 FIELD 3 - COLLECTING RAPPING MOTOR | ESP A CHBR 1 FLD 3 - HPR A TEMP | 3ESP-TE871B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD810 | ESP A CHAMBER 2 FIELD 3 - COLLECTING RAPPING MOTOR | ESP A CHBR 2 FLD 3 - HPR A TEMP | 3ESP-TE872A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD810 | ESP A CHAMBER 2 FIELD 3 - COLLECTING RAPPING MOTOR | ESP A CHBR 2 FLD 3 - HPR A TEMP | 3ESP-TE872B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD811 | ESP B CHAMBER 1 FIELD 3 - COLLECTING RAPPING MOTOR | ESP B CHBR 1 FLD 3 - HPR A TEMP | 3ESP-TE873A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD811 | ESP B CHAMBER 1 FIELD 3 - COLLECTING RAPPING MOTOR | ESP B CHBR 1 FLD 3 - HPR A TEMP | 3ESP-TE873B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD812 | ESP B CHAMBER 2 FIELD 3 - COLLECTING RAPPING MOTOR | ESP B CHBR 2 FLD 3 - HPR A TEMP | 3ESP-TE874A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD812 | ESP B CHAMBER 2 FIELD 3 - COLLECTING RAPPING MOTOR | ESP B CHBR 2 FLD 3 - HPR A TEMP | 3ESP-TE874B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD813 | ESP A CHAMBER 1 FIELD 4 - COLLECTING RAPPING MOTOR | ESP A CHBR 1 FLD 4 - HPR A TEMP | 3ESP-TE875A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD813 | ESP A CHAMBER 1 FIELD 4 - COLLECTING RAPPING MOTOR | ESP A CHBR 1 FLD 4 - HPR A TEMP | 3ESP-TE875B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD814 | ESP A CHAMBER 2 FIELD 4 - COLLECTING RAPPING MOTOR | ESP A CHBR 2 FLD 4 - HPR A TEMP | 3ESP-TE876A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD814 | ESP A CHAMBER 2 FIELD 4 - COLLECTING RAPPING MOTOR | ESP A CHBR 2 FLD 4 - HPR A TEMP | 3ESP-TE876B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD815 | ESP B CHAMBER 1 FIELD 4 - COLLECTING RAPPING MOTOR | ESP B CHBR 1 FLD 4 - HPR A TEMP | 3ESP-TE877A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD815 | ESP B CHAMBER 1 FIELD 4 - COLLECTING RAPPING MOTOR | ESP B CHBR 1 FLD 4 - HPR A TEMP | 3ESP-TE877B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD816 | ESP B CHAMBER 2 FIELD 4 - COLLECTING RAPPING MOTOR | ESP B CHBR 2 FLD 4 - HPR A TEMP | 3ESP-TE878A | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD816 | ESP B CHAMBER 2 FIELD 4 - COLLECTING RAPPING MOTOR | ESP B CHBR 2 FLD 4 - HPR A TEMP | 3ESP-TE878B | [14 empty] | 0
Air Flue Gas (AFG) | ESP | 3ESP-RD821 | ESP A CHAMBER 1 FIELD 1 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD822 | ESP A CHAMBER 2 FIELD 1 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD823 | ESP B CHAMBER 1 FIELD 1 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD824 | ESP B CHAMBER 2 FIELD 1 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD825 | ESP A CHAMBER 1 FIELD 2 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD826 | ESP A CHAMBER 2 FIELD 2 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD827 | ESP B CHAMBER 1 FIELD 2 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD828 | ESP B CHAMBER 2 FIELD 2 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD829 | ESP A CHAMBER 1 FIELD 3 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD830 | ESP A CHAMBER 2 FIELD 3 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD831 | ESP B CHAMBER 1 FIELD 3 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD832 | ESP B CHAMBER 2 FIELD 3 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD833 | ESP A CHAMBER 1 FIELD 4 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD834 | ESP A CHAMBER 2 FIELD 4 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD835 | ESP B CHAMBER 1 FIELD 4 - EMITTING RAPPING MOTOR
Air Flue Gas (AFG) | ESP | 3ESP-RD836 | ESP B CHAMBER 2 FIELD 4 - EMITTING RAPPING MOTOR
K3 & LH (KLH) | FF | 00FF-PAN001 | ELEC FIRE PMP CNTL PL CB | ELEC FIRE PMP CNTL PL CB CUR | 00FF-PAN001-A | [14 empty] | 0
Boiler (BOL) | FO | 00FO-M802A | LFO FWD PMP A MOTOR | LFO FWD PMP MTR CUR | 00FO-P802A-A | [14 empty] | 0
Boiler (BOL) | FO | 00FO-M802B | LFO FWD PMP B MOTOR | LFO FWD PMP MTR CUR | 00FO-P802B-A | [14 empty] | 0
Boiler (BOL) | FO | 00FO-P802A | LFO FWD PMP A
Boiler (BOL) | FO | 00FO-P802B | LFO FWD PMP B
Boiler (BOL) | FO | 3FO-T501 | ACCUMULATOR | FUEL OIL SUPPLY FLOW | 3FO-FIX501 | 1 | t/h | [10 empty] | 9-36t/h |  | F1DPw1kUu10ziUaXEx2rIyo4pAyQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZVRUwgT0lMIFNVUFBMWSBGTE9X
Boiler (BOL) | FO | 3FO-T502 | ACCUMULATOR | FUEL OIL SUPPLY FLOW | 3FO-FIX501-N | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAywwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZVRUwgT0lMIFNVUFBMWSBGTE9XIC1O
Boiler (BOL) | FO | 3FO-T503 | ACCUMULATOR | FUEL OIL BURNER HEADER PRESS | 3FO-PIX501 | 1 |  |  | 6barg |  |  | 0 |  | 999999 |  | 0 |  | 10-16barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAxgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZVRUwgT0lMIEJVUk5FUiBIRUFERVIgUFJFU1M
Boiler (BOL) | FO | 3FO-T504 | ACCUMULATOR | FUEL OIL BURNER SUPPLY HEADER TEMP | 3FO-TE501 | 1 |  |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  | >25°C |  | F1DPw1kUu10ziUaXEx2rIyo4pAxwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZVRUwgT0lMIEJVUk5FUiBTVVBQTFkgSEVBREVSIFRFTVA
Boiler (BOL) | FO | 3FO-T505 | ACCUMULATOR | LFO TK LVL | 00FO-LIX802
Boiler (BOL) | FO | 3FO-T506 | ACCUMULATOR | LFO TK ELEV 14.5M OIL TEMP | 00FO-TE802
Boiler (BOL) | FO | 3FO-T507 | ACCUMULATOR | LFO TK ELEV 7M OIL TEMP | 00FO-TE803
Boiler (BOL) | FO | 3FO-T508 | ACCUMULATOR | LFO TK ELEV 1M OIL TEMP | 00FO-TE804
Boiler (BOL) | FO | 3FO-T509 | ACCUMULATOR | UNIT3 EDG FODTK INL FLOW | 3FO-FIX001 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkVERyBGT0RUSyBJTkwgRkxX
Boiler (BOL) | FO | 3FO-T510 | ACCUMULATOR | UNIT3 EDG FODTK INL FLOW (m3/min) | 3FO-FIX001-INST
Boiler (BOL) | FO | EQUIPMENT UNKNOWN |  | LFO UNLD PMP A INL STR DP | 00FO-DPIX801A |  |  |  | -999999 |  |  |  |  | 350
Boiler (BOL) | FO | EQUIPMENT UNKNOWN |  | LFO UNLD PMP B INL STR DP | 00FO-DPIX801B |  |  |  | -999999 |  |  |  |  | 350
Boiler (BOL) | FO | EQUIPMENT UNKNOWN |  | LFO FWD PMP INL HDR STR DP | 00FO-DPIX803
Boiler (BOL) | FO | EQUIPMENT UNKNOWN |  | LFO FWD PMP OUTL HDR PRESS | 00FO-PIX801
Boiler (BOL) | FO | EQUIPMENT UNKNOWN |  | LFO FWD PMP OUTL HDR TEMP | 00FO-TE801
Feedwater (FW) | FW | 3FW-AU030A | TBFP A REDUCTION GEAR | TBFP GR BOX BRG 1 MET TEMP | 3FW-TE028A | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAkw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBHUiBCT1ggQlJHIDEgTUVUIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU030A | TBFP A REDUCTION GEAR | TBFP GR BOX BRG 2 MET TEMP | 3FW-TE029A | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAlA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBHUiBCT1ggQlJHIDIgTUVUIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU030A | TBFP A REDUCTION GEAR | TBFP GR BOX BRG 3 MET TEMP | 3FW-TE030A | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAlQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBHUiBCT1ggQlJHIDMgTUVUIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU030A | TBFP A REDUCTION GEAR | TBFP GR BOX BRG 4 MET TEMP | 3FW-TE031A | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAlg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBHUiBCT1ggQlJHIDQgTUVUIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU030B | TBFP B REDUCTION GEAR | TBFP GR BOX BRG 1 MET TEMP | 3FW-TE028B | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAqg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBHUiBCT1ggQlJHIDEgTUVUIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU030B | TBFP B REDUCTION GEAR | TBFP GR BOX BRG 2 MET TEMP | 3FW-TE029B | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAqw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBHUiBCT1ggQlJHIDIgTUVUIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU030B | TBFP B REDUCTION GEAR | TBFP GR BOX BRG 3 MET TEMP | 3FW-TE030B | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pArA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBHUiBCT1ggQlJHIDMgTUVUIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU030B | TBFP B REDUCTION GEAR | TBFP GR BOX BRG 4 MET TEMP | 3FW-TE031B | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pArQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBHUiBCT1ggQlJHIDQgTUVUIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU330 | MBFP FLUID COUPLING | MBFP HYDR CPLG BRG 1 TEMP | 3FW-TE328 | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAKQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgSFlEUiBDUExHIEJSRyAxIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU331 | MBFP FLUID COUPLING | MBFP HYDR CPLG BRG 2 TEMP | 3FW-TE329 | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAKg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgSFlEUiBDUExHIEJSRyAyIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU332 | MBFP FLUID COUPLING | MBFP HYDR CPLG BRG 3 TEMP | 3FW-TE330 | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAKw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgSFlEUiBDUExHIEJSRyAzIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU333 | MBFP FLUID COUPLING | MBFP HYDR CPLG BRG 4 TEMP | 3FW-TE331 | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pALA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgSFlEUiBDUExHIEJSRyA0IFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-AU334 | MBFP FLUID COUPLING | MBFP HYDR CPLG BRG 6 TEMP | 3FW-TE332 | 1 |  |  | -999999 |  |  | 0 |  | 85 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pALg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgSFlEUiBDUExHIEJSRyA2IFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-M320 | MBFP MOTOR A | MBFP MTR A CUR | 3FW-P300-A1 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAPw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTVRSIEEgQ1VS
Feedwater (FW) | FW | 3FW-M321 | MBFP MOTOR B | MBFP MTR B CUR | 3FW-P300-A2 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAPw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTVRSIEEgQ1VS |  | 1
Feedwater (FW) | FW | 3FW-M320 | MBFP MOTOR A | MBFP MTR WDG TEMP U | 3FW-TE310 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 125 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfRYAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUC5NQkZQIE1PVE9SIEEgV0lORElORyBURU1QIFU |  | 1
Feedwater (FW) | FW | 3FW-M320 | MBFP MOTOR A | MBFP MTR WDG TEMP V | 3FW-TE312 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 125 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfhYAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUC5NQkZQIE1PVE9SIEEgV0lORElORyBURU1QIFY |  | 1
Feedwater (FW) | FW | 3FW-M320 | MBFP MOTOR A | MBFP MTR WDG TEMP W | 3FW-TE314 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 125 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfxYAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUC5NQkZQIE1PVE9SIEEgV0lORElORyBURU1QIFc |  | 1
Feedwater (FW) | FW | 3FW-M320 | MBFP MOTOR A | MBFP MTR BRG 1 TEMP | 3FW-TE322 | 1 |  |  | -999999 |  |  | 0 |  | 95 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAPQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTVRSIEEgQlJHIDEgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-M320 | MBFP MOTOR A | MBFP MTR BRG 2 TEMP | 3FW-TE323 | 1 |  |  | -999999 |  |  | 0 |  | 95 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAPg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTVRSIEEgQlJHIDIgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-M321 | MBFP MOTOR B | MBFP MTR CUR | 3FW-P300-A3 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pARQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTVRSIEIgQ1VS |  | 1
Feedwater (FW) | FW | 3FW-M321 | MBFP MOTOR B | MBFP MTR WDG TEMP U | 3FW-TE316 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 125 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAgBYAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUC5NQkZQIE1PVE9SIEIgV0lORElORyBURU1QIFU |  | 1
Feedwater (FW) | FW | 3FW-M321 | MBFP MOTOR B | MBFP MTR WDG TEMP V | 3FW-TE318 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 125 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAgRYAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUC5NQkZQIE1PVE9SIEIgV0lORElORyBURU1QIFY |  | 1
Feedwater (FW) | FW | 3FW-M321 | MBFP MOTOR B | MBFP MTR WDG TEMP W | 3FW-TE320 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 125 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAghYAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUC5NQkZQIE1PVE9SIEIgV0lORElORyBURU1QIFc |  | 1
Feedwater (FW) | FW | 3FW-M321 | MBFP MOTOR B | MBFP MTR BRG 1 TEMP | 3FW-TE324 | 1 |  |  | -999999 |  |  | 0 |  | 95 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAQw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTVRSIEIgQlJHIDEgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-M321 | MBFP MOTOR B | MBFP MTR BRG 2 TEMP | 3FW-TE325 | 1 |  |  | -999999 |  |  | 0 |  | 95 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pARA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTVRSIEIgQlJHIDIgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P010A | TURBINE DRIVEN BOILER FEEDWATER PUMP A | TBFP BRG 1 MET TEMP | 3FW-TE026A | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAjQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBCUkcgMSBNRVQgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P010A | TURBINE DRIVEN BOILER FEEDWATER PUMP A | TBFP BRG 2 MET TEMP | 3FW-TE027A | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAjg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBCUkcgMiBNRVQgVEVNUA |  | 1
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A THRST BRG RTN OIL TEMP | 3LOT-TE006A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAnw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBUSFJTVCBCUkcgUlROIE9JTCBURU1Q
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A BP THRST BRG RTN OIL TEMP | 3LOT-TE007A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBCUCBUSFJTVCBCUkcgUlROIE9JTCBURU1Q
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A OUTL FLW | 3UCSA-CALC202 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAnA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBPVVRMIEZMVw
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A OUTL FLW CNTL DEVN | 3UCSA-CALC211 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAnQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBPVVRMIEZMVyBDTlRMIERFVk4
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A DIFF PRESS CNTL SV | 3UCSA-CALC212 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBESUZGIFBSRVNTIENOVEwgU1Y
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A DIFF PRESS | 3UCSA-CALC214 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBESUZGIFBSRVNT
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A DIFF PRESS CNTL DEVN | 3UCSA-CALC215 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBESUZGIFBSRVNTIENOVEwgREVWTg
Feedwater (FW) | FW | 3FW-P010A | TURBINE DRIVEN BOILER FEEDWATER PUMP A | TBFP INL STR DP | 3FW-DPIX001A | 1 |  |  | -999999 |  |  | 0 |  | 0.5 | 0-1.5bar | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBJTkwgU1RSIERQ |  | 1
Feedwater (FW) | FW | 3FW-P010A | TURBINE DRIVEN BOILER FEEDWATER PUMP A | TBFP INL FW FLW | 3FW-FIX001A-N | 1 | t/h |  |  |  |  | 2/4/0 |  | ketemu tag, tapi tidak ada info threshold |  | 0/0/0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAlw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBJTkwgRlcgRkxX |  | 1
Feedwater (FW) | FW | 3FW-P010A | TURBINE DRIVEN BOILER FEEDWATER PUMP A | TBFP OUTL FW PRESS | 3FW-PIX002A | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-400barg | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAng8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBPVVRMIEZXIFBSRVNT |  | 1
Feedwater (FW) | FW | 3FW-P010A | TURBINE DRIVEN BOILER FEEDWATER PUMP A | TBFP INL FW TEMP | 3FW-TE002A | 1 | [8 empty] | 0-250 degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBJTkwgRlcgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P010A | TURBINE DRIVEN BOILER FEEDWATER PUMP A | TBFP A LWR BRL TEMP | 3FW-TE007A | 1 | [8 empty] | 0-200 degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBMV1IgQlJMIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-P010A | TURBINE DRIVEN BOILER FEEDWATER PUMP A | TBFP A UPR BRL TEMP | 3FW-TE008A | 1 | [8 empty] | 0-200 degC |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAoA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBVUFIgQlJMIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-P010B | TURBINE DRIVEN BOILER FEEDWATER PUMP B | TBFP BRG 1 MET TEMP | 3FW-TE026B | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-100 degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pApA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBCUkcgMSBNRVQgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P010B | TURBINE DRIVEN BOILER FEEDWATER PUMP B | TBFP BRG 2 MET TEMP | 3FW-TE027B | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-100 degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pApQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBCUkcgMiBNRVQgVEVNUA |  | 1
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B THRST BRG RTN OIL TEMP | 3LOT-TE006B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBUSFJTVCBCUkcgUlROIE9JTCBURU1Q
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B BP THRST BRG RTN OIL TEMP | 3LOT-TE007B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAow8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBCUCBUSFJTVCBCUkcgUlROIE9JTCBURU1Q
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B OUTL FLW | 3UCSA-CALC203 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAsw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBPVVRMIEZMVw
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B OUTL FLW CNTL DEVN | 3UCSA-CALC216 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBPVVRMIEZMVyBDTlRMIERFVk4
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B DIFF PRESS CNTL SV | 3UCSA-CALC217 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAqQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBESUZGIFBSRVNTIENOVEwgU1Y
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B DIFF PRESS | 3UCSA-CALC219 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pApg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBESUZGIFBSRVNT
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B DIFF PRESS CNTL DEVN | 3UCSA-CALC220 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pApw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBESUZGIFBSRVNTIENOVEwgREVWTg
Feedwater (FW) | FW | 3FW-P010B | TURBINE DRIVEN BOILER FEEDWATER PUMP B | TBFP INL STR DP | 3FW-DPIX001B | 1 |  |  | -999999 |  |  | 0 |  | 0.5 | 0-1.5bar | 0 |  | Now: 0.216bar |  | F1DPw1kUu10ziUaXEx2rIyo4pAsA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBJTkwgU1RSIERQ |  | 1
Feedwater (FW) | FW | 3FW-P010B | TURBINE DRIVEN BOILER FEEDWATER PUMP B | TBFP INL FW FLW | 3FW-FIX001B-N | 1 | t/h |  |  |  |  | 2/4/0 |  |  |  | 0/0/0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pArg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBJTkwgRlcgRkxX |  | 1
Feedwater (FW) | FW | 3FW-P010B | TURBINE DRIVEN BOILER FEEDWATER PUMP B | TBFP OUTL FW PRESS | 3FW-PIX002B | 1 |  |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAtQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBPVVRMIEZXIFBSRVNT |  | 1
Feedwater (FW) | FW | 3FW-P010B | TURBINE DRIVEN BOILER FEEDWATER PUMP B | TBFP INL FW TEMP | 3FW-TE002B | 1 | [8 empty] | 0-250degC |  |  | Now: 169.8degC |  | F1DPw1kUu10ziUaXEx2rIyo4pArw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBJTkwgRlcgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P010B | TURBINE DRIVEN BOILER FEEDWATER PUMP B | TBFP A LWR BRL TEMP | 3FW-TE007B | 1 | [8 empty] | 0-200degC |  |  | Now: 158.5degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAsQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBMV1IgQlJMIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-P010B | TURBINE DRIVEN BOILER FEEDWATER PUMP B | TBFP A UPR BRL TEMP | 3FW-TE008B | 1 | [8 empty] | 0-200degC |  |  | Now: 163.1degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAtw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBVUFIgQlJMIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-P020A | TBFP A BOOSTER PUMP | TBFP BP BRG 1 MET TEMP | 3FW-TE033A | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-100degC | 0 |  | Now: 51.7degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAig8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBCUCBCUkcgMSBNRVQgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P020A | TBFP A BOOSTER PUMP | TBFP BP BRG 2 MET TEMP | 3FW-TE034A | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAiw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBCUCBCUkcgMiBNRVQgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P020B | TBFP B BOOSTER PUMP | TBFP BP BRG 1 MET TEMP | 3FW-TE033B | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAoQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBCUCBCUkcgMSBNRVQgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P020B | TBFP B BOOSTER PUMP | TBFP BP BRG 2 MET TEMP | 3FW-TE034B | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-100degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAog8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBCUCBCUkcgMiBNRVQgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P300 | MOTOR DRIVEN BOILER FEEDWATER PUMP | MBFP INL STR DP | 3FW-DPIX301 | 1 |  |  | -999999 |  |  | 0 |  | 0.5 | 0-1.5bar | 0 |  | Now: 0.0 bar |  | F1DPw1kUu10ziUaXEx2rIyo4pAMw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgSU5MIFNUUiBEUA |  | 1
Feedwater (FW) | FW | 3FW-P301 | MOTOR DRIVEN BOILER FEEDWATER PUMP | MBFP INL FW FLW | 3FW-FIX301-N | 1 | [5 empty] | 2/4/0 |  |  |  | 0/0/0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAMQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgSU5MIEZXIEZMVw |  | 1
Feedwater (FW) | FW | 3FW-P302 | MOTOR DRIVEN BOILER FEEDWATER PUMP | MBFP BRG 1 TEMP | 3FW-TE333 | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-100degC | 0 |  | Now: 66.8 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAJQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgQlJHIDEgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P303 | MOTOR DRIVEN BOILER FEEDWATER PUMP | MBFP BRG 2 TEMP | 3FW-TE334 | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-100degC | 0 |  | Now: 45.9degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAJg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgQlJHIDIgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P304 | MOTOR DRIVEN BOILER FEEDWATER PUMP | MBFP INL FW TEMP | 3FW-TE302 | 1 | [8 empty] | 0-250degC |  |  | Now: 160.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAMg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgSU5MIEZXIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-P305 | MOTOR DRIVEN BOILER FEEDWATER PUMP | MBFP LWR BRL TEMP | 3FW-TE307 | 1 | [8 empty] | 0-200degC |  |  | Now: 132.4degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAOw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTFdSIEJSTCBURU1Q |  | 1
Feedwater (FW) | FW | 3FW-P306 | MOTOR DRIVEN BOILER FEEDWATER PUMP | MBFP UPR BRL TEMP | 3FW-TE308 | 1 | [8 empty] | 0-200degC |  |  | Now: 154.4degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAUA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgVVBSIEJSTCBURU1Q |  | 1
Feedwater (FW) | FW | 3FW-P307 | MOTOR DRIVEN BOILER FEEDWATER PUMP | BFP OUTL FW PRESS | 3FW-PIX003 | 1 |  |  | -999999 |  |  | 0 |  | 220 | 0-300barg | 0 |  | Now: 205degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAxwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUCBPVVRMIEZXIFBSRVNT |  | 1
Feedwater (FW) | FW | 3FW-P308 | MOTOR DRIVEN BOILER FEEDWATER PUMP | MBFP OUTL FW PRESS | 3FW-PIX302 | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-400barg | 0 |  | Now: 9.3bar |  | F1DPw1kUu10ziUaXEx2rIyo4pATQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgT1VUTCBGVyBQUkVTUw |  | 1
Feedwater (FW) | FW | 3FW-P309 | MOTOR DRIVEN BOILER FEEDWATER PUMP | MBFP SPD | 3FW-SE301 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pATg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgU1BE |  | 1
Feedwater (FW) | FW | 3FW-P310 | MOTOR DRIVEN BOILER FEEDWATER PUMP | BFP OUTL FW TEMP | 3FW-TE003 | 1 | [8 empty] | 0-250degC |  |  | Now: 173.4degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAyAoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUCBPVVRMIEZXIFRFTVA |  | 1
Feedwater (FW) | FW | 3FW-P310 | MBFP BOOSTER PUMP | MBFP BP BRG 1 TEMP | 3FW-TE326 | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-100degC | 0 |  | Now: 52.3degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAIg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgQlAgQlJHIDEgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-P311 | MBFP BOOSTER PUMP | MBFP BP BRG 2 TEMP | 3FW-TE327 | 1 |  |  | -999999 |  |  | 0 |  | 80 | 0-100degC | 0 |  | Now: 56.8degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAIw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgQlAgQlJHIDIgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-H050 | HP FEEDWATER HEATER NO.5 | HP FW HTR 5 LVL | 3FW-LIX003A | 1 |  |  | -50 | -999999 |  |  |  | 160 | 210 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pATw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQIEZXIEhUUiA1IExWTCBB |  | 1
Feedwater (FW) | FW | 3FW-H051 | HP FEEDWATER HEATER NO.5 | HP FW HTR 5 LVL | 3FW-LIX003B | 1 |  |  | -50 | -999999 |  |  |  | 160 | 210 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAUA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQIEZXIEhUUiA1IExWTCBC |  | 1
Feedwater (FW) | FW | 3FW-H052 | HP FEEDWATER HEATER NO.5 | HP FW HTR 5 OUTL FW TEMP | 3FW-TE004 | 1 | [8 empty] | 0-300barg |  |  | Now: 205.4degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAUQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQIEZXIEhUUiA1IE9VVEwgRlcgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-H060 | HP FEEDWATER HEATER NO.6 | HP FW HTR 6 LVL | 3FW-LIX002A | 1 |  |  | -50 | -999999 |  |  |  | 160 | 210 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAWA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQIEZXIEhUUiA2IExWTCBB |  | 1
Feedwater (FW) | FW | 3FW-H061 | HP FEEDWATER HEATER NO.6 | HP FW HTR 6 LVL | 3FW-LIX002B | 1 |  |  | -50 | -999999 |  |  |  | 160 | 210 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAWQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQIEZXIEhUUiA2IExWTCBC |  | 1
Feedwater (FW) | FW | 3FW-H062 | HP FEEDWATER HEATER NO.6 | HP FW HTR 6 OUTL FW TEMP | 3FW-TE005 | 1 | [8 empty] | 0-300barg |  |  | Now: 246.4degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAWg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQIEZXIEhUUiA2IE9VVEwgRlcgVEVNUA |  | 1
Feedwater (FW) | FW | 3FW-H070 | HP FEEDWATER HEATER NO.7 | HP FW HTR 7 LVL | 3FW-LIX001A | 1 |  |  | -50 | -999999 |  |  |  | 160 | 210 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAYg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQIEZXIEhUUiA3IExWTCBB |  | 1
Feedwater (FW) | FW | 3FW-H071 | HP FEEDWATER HEATER NO.7 | HP FW HTR 7 LVL | 3FW-LIX001B | 1 |  |  | -50 | -999999 |  |  |  | 160 | 210 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAYw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQIEZXIEhUUiA3IExWTCBC |  | 1
Feedwater (FW) | FW | 3FW-H072 | HP FEEDWATER HEATER NO.7 | HP FW HTR 7 OUTL FW TEMP | 3FW-TE006 | 1 | [8 empty] | 0-300barg |  |  | Now: 287.1degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAZA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQIEZXIEhUUiA3IE9VVEwgRlcgVEVNUA |  | 1
Generator (GEN) | GEN | 3GEN-M101A | THYRISTOR COOLING FAN MOTOR-A-1 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M101B | THYRISTOR COOLING FAN MOTOR-B-1 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M102A | THYRISTOR COOLING FAN MOTOR-A-2 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M102B | THYRISTOR COOLING FAN MOTOR-B-2 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M103A | THYRISTOR COOLING FAN MOTOR-A-3 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M103B | THYRISTOR COOLING FAN MOTOR-B-3 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M201A | GMCB COOLING FAN MOTOR-A |  | NO TAG
Generator (GEN) | GEN | 3GEN-M202A | GMCB COOLING FAN MOTOR-B |  | NO TAG
Generator (GEN) | GEN | 3GEN-M203A | GMCB COOLING FAN MOTOR-C |  | NO TAG
Generator (GEN) | GEN | 3GEN-M204A | GMCB COOLING FAN MOTOR-D |  | NO TAG
Generator (GEN) | GEN | 3GEN-M205A | GMCB COOLING FAN MOTOR-E |  | NO TAG
Generator (GEN) | GEN | 3GEN-M206A | GMCB COOLING FAN MOTOR-F |  | NO TAG
Generator (GEN) | GEN | 3GEN-M211A | GMCB RADIATOR COOLING FAN MOTOR-A1 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M211B | GMCB RADIATOR COOLING FAN MOTOR-B1 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M211C | GMCB RADIATOR COOLING FAN MOTOR-C1 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M212A | GMCB RADIATOR COOLING FAN MOTOR-A2 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M212B | GMCB RADIATOR COOLING FAN MOTOR-B2 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M212C | GMCB RADIATOR COOLING FAN MOTOR-C2 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M213A | GMCB RADIATOR COOLING FAN MOTOR-A3 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M213B | GMCB RADIATOR COOLING FAN MOTOR-B3 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M213C | GMCB RADIATOR COOLING FAN MOTOR-C3 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M214A | GMCB RADIATOR COOLING FAN MOTOR-A4 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M214B | GMCB RADIATOR COOLING FAN MOTOR-B4 |  | NO TAG
Generator (GEN) | GEN | 3GEN-M214C | GMCB RADIATOR COOLING FAN MOTOR-C4 |  | NO TAG
Generator (GEN) | GEN | 3GEN-GM002 | GENERATOR | GEN H2 CLR A OUTL GAS TEMP (CLD GAS) | 3GEN-TE022 | 1 |  |  | -999999 |  |  | 0 |  | 50 |  | 0 |  | Now: 38.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA4wwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBIMiBDTFIgQSBPVVRMIEdBUyBURU1QIChDTEQgR0FTKQ |  | 1
Generator (GEN) | GEN | 3GEN-GM003 | GENERATOR | GEN H2 CLR A OUTL GAS TEMP (CLD GAS) | 3GEN-TE024 | 1 |  |  | -999999 |  |  | 0 |  | 50 |  | 0 |  | Now: 38.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA5QwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBIMiBDTFIgQiBPVVRMIEdBUyBURU1QIChDTEQgR0FTKQ |  | 1
Generator (GEN) | GEN | 3GEN-GM004 | GENERATOR | GEN H2 CLR A OUTL GAS TEMP (CLD GAS) | 3GEN-TE021 | 1 |  |  | -999999 |  |  | 0 |  | 50 |  | 0 |  | Now: 39degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA5wwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBIMiBDTFIgQyBPVVRMIEdBUyBURU1QIChDTEQgR0FTKQ |  | 1
Generator (GEN) | GEN | 3GEN-GM005 | GENERATOR | GEN H2 CLR A OUTL GAS TEMP (CLD GAS) | 3GEN-TE023 | 1 |  |  | -999999 |  |  | 0 |  | 50 |  | 0 |  | Now: 38.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA6QwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBIMiBDTFIgRCBPVVRMIEdBUyBURU1QIChDTEQgR0FTKQ |  | 1
Generator (GEN) | GEN | 3GEN-GM001 | GENERATOR | GEN H2 CLR A INL GAS TEMP (HOT GAS) | 3GEN-TE026 | 1 |  |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  | Now: 56.1degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA4gwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBIMiBDTFIgQSBJTkwgR0FTIFRFTVAgKEhPVCBHQVMp |  | 1
Generator (GEN) | GEN | 3GEN-GM002 | GENERATOR | GEN H2 CLR A INL GAS TEMP (HOT GAS) | 3GEN-TE028 | 1 |  |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  | Now: 56.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA5AwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBIMiBDTFIgQiBJTkwgR0FTIFRFTVAgKEhPVCBHQVMp |  | 1
Generator (GEN) | GEN | 3GEN-GM003 | GENERATOR | GEN H2 CLR A INL GAS TEMP (HOT GAS) | 3GEN-TE025 | 1 |  |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  | Now: 55.3degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA5gwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBIMiBDTFIgQyBJTkwgR0FTIFRFTVAgKEhPVCBHQVMp |  | 1
Generator (GEN) | GEN | 3GEN-GM004 | GENERATOR | GEN H2 CLR A INL GAS TEMP (HOT GAS) | 3GEN-TE027 | 1 |  |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  | Now: 57degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA6AwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBIMiBDTFIgRCBJTkwgR0FTIFRFTVAgKEhPVCBHQVMp |  | 1
Generator (GEN) | GEN | 3GEN-GM000 | GENERATOR | SYN PHAS DIFF | 3GEN-HSIG062 | 1 | rad | [12 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAiQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNZTiBQSEFTIERJRkY |  | 1
Generator (GEN) | GEN | 3GEN-GM001 | GENERATOR | GT LV SIDE V U-W | 3GEN-HSIG063 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAPA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdUIExWIFNJREUgViBVLVc |  | 1
Generator (GEN) | GEN | 3GEN-GM002 | GENERATOR | GEN TERM V U-V | 3GEN-HSIG064 | 1 | kV | [12 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAKw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBURVJNIFYgVS1W |  | 1
Generator (GEN) | GEN | 3GEN-GM003 | GENERATOR | GEN TERM V V-W | 3GEN-HSIG065 | 1 | kV | [12 empty] | F1DPw1kUu10ziUaXEx2rIyo4pALA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBURVJNIFYgVi1X |  | 1
Generator (GEN) | GEN | 3GEN-GM004 | GENERATOR | GEN TERM V W-U | 3GEN-HSIG066 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pALQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBURVJNIFYgVy1V |  | 1
Generator (GEN) | GEN | 3GEN-GM005 | GENERATOR | GEN CUR U | 3GEN-HSIG067 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA3AwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBDVVIgVQ |  | 1
Generator (GEN) | GEN | 3GEN-GM006 | GENERATOR | GEN CUR V | 3GEN-HSIG068 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA3QwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBDVVIgVg |  | 1
Generator (GEN) | GEN | 3GEN-GM007 | GENERATOR | GEN CUR W | 3GEN-HSIG069 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA3gwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBDVVIgVw |  | 1
Generator (GEN) | GEN | 3GEN-GM008 | GENERATOR | GEN OPUT PWR | 3GEN-HSIG070 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA8AwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBPUFVUIFBXUg |  | 1
Generator (GEN) | GEN | 3GEN-GM009 | GENERATOR | GEN OPUT VAR | 3GEN-HSIG071 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA8QwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBPUFVUIFZBUg |  | 1
Generator (GEN) | GEN | 3GEN-GM010 | GENERATOR | GEN PF | 3GEN-HSIG072 | 1 | PF | [12 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA8gwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBQRg |  | 1
Generator (GEN) | GEN | 3GEN-GM011 | GENERATOR | GEN OPUT FREQ | 3GEN-HSIG073 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA7wwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBPUFVUIEZSRVE |  | 1
Generator (GEN) | GEN | 3GEN-GM012 | GENERATOR | GENERATOR FREQ | 3GEN-HSIG093 | 1 | Hz |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAMQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTkVSQVRPUiBGUkVR |  | 1
Generator (GEN) | GEN | 3GEN-GM013 | GENERATOR | GEN STAT COIL TEMP (V3) | 3GEN-TE003 | 1 |  |  | -999999 |  |  | 0 |  | 100 | 0-150degC | 0 |  | Now: 69.2degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAJw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgVEVNUCAoVjMp |  | 1
Generator (GEN) | GEN | 3GEN-GM014 | GENERATOR | GEN STAT COIL TEMP (U3) | 3GEN-TE007 | 1 |  |  | -999999 |  |  | 0 |  | 100 | 0-150degC | 0 |  | Now: 68.4degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAJg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgVEVNUCAoVTMp |  | 1
Generator (GEN) | GEN | 3GEN-GM015 | GENERATOR | GEN STAT COIL TEMP (W3) | 3GEN-TE011 | 1 |  |  | -999999 |  |  | 0 |  | 100 | 0-150degC | 0 |  | Now: 67.2degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAKA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgVEVNUCAoVzMp |  | 1
Generator (GEN) | GEN | 3GEN-GM016 | GENERATOR | GEN STAT CORE TEMP (CTC1) | 3GEN-TE013 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 0-150degC | 0 | 0 | Now: 75.8degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAKQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPUkUgVEVNUCAoQ1RDMSk |  | 1
Generator (GEN) | GEN | 3GEN-GM017 | GENERATOR | GEN STAT CORE TEMP (CTC2) | 3GEN-TE014 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 999999 | 0-150degC | 0 | 0 | Now: 68.2degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAKg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPUkUgVEVNUCAoQ1RDMik |  | 1
Generator (GEN) | GEN | 3GEN-GM018 | GENERATOR | GEN COLL OUTL AIR TEMP | 3GEN-TE029 | 1 |  |  | -999999 |  |  | 0 |  | 65 | 0-150degC | 0 |  | Now: 36.2degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA2wwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBDT0xMIE9VVEwgQUlSIFRFTVA |  | 1
Generator (GEN) | GEN | 3GEN-GM019 | GENERATOR | GEN COLL INL AIR TEMP | 3GEN-TE030 | 1 |  |  | -999999 | -999999 |  | 0 |  |  | 0-150degC | 0 |  | Now: 44.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA2gwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBDT0xMIElOTCBBSVIgVEVNUA |  | 1
Generator (GEN) | GEN | 3GEN-GM020 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC1) | 3GEN-TE031 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA9gwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMSk |  | 1
Generator (GEN) | GEN | 3GEN-GM021 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC2) | 3GEN-TE032 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAAQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMik |  | 1
Generator (GEN) | GEN | 3GEN-GM022 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC3) | 3GEN-TE033 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pADA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMyk |  | 1
Generator (GEN) | GEN | 3GEN-GM023 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC4) | 3GEN-TE034 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAFw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNCk |  | 1
Generator (GEN) | GEN | 3GEN-GM024 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC5) | 3GEN-TE035 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAIQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNSk |  | 1
Generator (GEN) | GEN | 3GEN-GM025 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC6) | 3GEN-TE036 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAIg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNik |  | 1
Generator (GEN) | GEN | 3GEN-GM026 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC7) | 3GEN-TE037 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAIw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNyk |  | 1
Generator (GEN) | GEN | 3GEN-GM027 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC8) | 3GEN-TE038 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAJA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDOCk |  | 1
Generator (GEN) | GEN | 3GEN-GM028 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC9) | 3GEN-TE039 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAJQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDOSk |  | 1
Generator (GEN) | GEN | 3GEN-GM029 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC10) | 3GEN-TE040 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA9wwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMTAp |  | 1
Generator (GEN) | GEN | 3GEN-GM030 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC11) | 3GEN-TE041 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA-AwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMTEp |  | 1
Generator (GEN) | GEN | 3GEN-GM031 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC12) | 3GEN-TE042 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA-QwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMTIp |  | 1
Generator (GEN) | GEN | 3GEN-GM032 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC13) | 3GEN-TE043 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA-gwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMTMp |  | 1
Generator (GEN) | GEN | 3GEN-GM033 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC14) | 3GEN-TE044 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA-wwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMTQp |  | 1
Generator (GEN) | GEN | 3GEN-GM034 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC15) | 3GEN-TE045 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA_AwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMTUp |  | 1
Generator (GEN) | GEN | 3GEN-GM035 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC16) | 3GEN-TE046 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA_QwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMTYp |  | 1
Generator (GEN) | GEN | 3GEN-GM036 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC17) | 3GEN-TE047 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA_gwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMTcp |  | 1
Generator (GEN) | GEN | 3GEN-GM037 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC18) | 3GEN-TE048 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA_wwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMTgp |  | 1
Generator (GEN) | GEN | 3GEN-GM038 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC19) | 3GEN-TE049 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAAA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMTkp |  | 1
Generator (GEN) | GEN | 3GEN-GM039 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC20) | 3GEN-TE050 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAAg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMjAp |  | 1
Generator (GEN) | GEN | 3GEN-GM040 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC21) | 3GEN-TE051 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAAw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMjEp |  | 1
Generator (GEN) | GEN | 3GEN-GM041 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC22) | 3GEN-TE052 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pABA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMjIp |  | 1
Generator (GEN) | GEN | 3GEN-GM042 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC23) | 3GEN-TE053 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pABQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMjMp |  | 1
Generator (GEN) | GEN | 3GEN-GM043 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC24) | 3GEN-TE054 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pABg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMjQp |  | 1
Generator (GEN) | GEN | 3GEN-GM044 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC25) | 3GEN-TE055 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pABw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMjUp |  | 1
Generator (GEN) | GEN | 3GEN-GM045 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC26) | 3GEN-TE056 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pACA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMjYp |  | 1
Generator (GEN) | GEN | 3GEN-GM046 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC27) | 3GEN-TE057 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pACQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMjcp |  | 1
Generator (GEN) | GEN | 3GEN-GM047 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC28) | 3GEN-TE058 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pACg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMjgp |  | 1
Generator (GEN) | GEN | 3GEN-GM048 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC29) | 3GEN-TE059 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pACw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMjkp |  | 1
Generator (GEN) | GEN | 3GEN-GM049 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC30) | 3GEN-TE060 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pADQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMzAp |  | 1
Generator (GEN) | GEN | 3GEN-GM050 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC31) | 3GEN-TE061 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pADg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMzEp |  | 1
Generator (GEN) | GEN | 3GEN-GM051 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC32) | 3GEN-TE062 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pADw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMzIp |  | 1
Generator (GEN) | GEN | 3GEN-GM052 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC33) | 3GEN-TE063 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAEA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMzMp |  | 1
Generator (GEN) | GEN | 3GEN-GM053 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC34) | 3GEN-TE064 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAEQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMzQp |  | 1
Generator (GEN) | GEN | 3GEN-GM054 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC35) | 3GEN-TE065 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAEg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMzUp |  | 1
Generator (GEN) | GEN | 3GEN-GM055 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC36) | 3GEN-TE066 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAEw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMzYp |  | 1
Generator (GEN) | GEN | 3GEN-GM056 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC37) | 3GEN-TE067 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAFA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMzcp |  | 1
Generator (GEN) | GEN | 3GEN-GM057 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC38) | 3GEN-TE068 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAFQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMzgp |  | 1
Generator (GEN) | GEN | 3GEN-GM058 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC39) | 3GEN-TE069 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAFg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDMzkp |  | 1
Generator (GEN) | GEN | 3GEN-GM059 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC40) | 3GEN-TE070 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAGA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNDAp |  | 1
Generator (GEN) | GEN | 3GEN-GM060 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC41) | 3GEN-TE071 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAGQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNDEp |  | 1
Generator (GEN) | GEN | 3GEN-GM061 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC42) | 3GEN-TE072 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAGg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNDIp |  | 1
Generator (GEN) | GEN | 3GEN-GM062 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC43) | 3GEN-TE073 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAGw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNDMp |  | 1
Generator (GEN) | GEN | 3GEN-GM063 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC44) | 3GEN-TE074 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAHA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNDQp |  | 1
Generator (GEN) | GEN | 3GEN-GM064 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC45) | 3GEN-TE075 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAHQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNDUp |  | 1
Generator (GEN) | GEN | 3GEN-GM065 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC46) | 3GEN-TE076 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAHg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNDYp |  | 1
Generator (GEN) | GEN | 3GEN-GM066 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC47) | 3GEN-TE077 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAHw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNDcp |  | 1
Generator (GEN) | GEN | 3GEN-GM067 | GENERATOR | GEN STAT COIL CLG WTR OUTL TEMP (TC48) | 3GEN-TE078 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 95 | 0 | 0 | Now: 57.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAIA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTiBTVEFUIENPSUwgQ0xHIFdUUiBPVVRMIFRFTVAgKFRDNDgp |  | 1
Generator (GEN) | GEN | 3GEN-GM074 | GENERATOR | BRG 9 MET TEMP | 3GEN-TE079 | 1 |  |  | -999999 |  |  | 0 |  | 107 | 0-150degC | 0 |  | Now: 84.4degC |  | F1DPw1kUu10ziUaXEx2rIyo4pATQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA5IE1FVCBURU1Q |  | 1
Generator (GEN) | GEN | 3GEN-GM075 | GENERATOR | BRG 10 MET TEMP | 3GEN-TE080 | 1 |  |  | -999999 |  |  | 0 |  | 107 | 0-150degC | 0 |  | Now: 83.6degC |  | F1DPw1kUu10ziUaXEx2rIyo4pALQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAxMCBNRVQgVEVNUA |  | 1
Generator (GEN) | GEN | 3GEN-GM076 | GENERATOR | BRG 9 VIBN X | 3GEN-VE001A | 1 | µmpp |  |  |  |  | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pATwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA5IFZJQk4gWA |  | 1
Generator (GEN) | GEN | 3GEN-GM077 | GENERATOR | BRG 9 VIBN Y | 3GEN-VE001B | 1 | µmpp |  |  |  |  | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAUAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA5IFZJQk4gWQ |  | 1
Generator (GEN) | GEN | 3GEN-GM078 | GENERATOR | BRG 10 VIBN X | 3GEN-VE002A | 1 | [5 empty] | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pALwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAxMCBWSUJOIFg |  | 1
Generator (GEN) | GEN | 3GEN-GM079 | GENERATOR | BRG 10 VIBN Y | 3GEN-VE002B | 1 | µmpp |  |  |  |  | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAMAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAxMCBWSUJOIFk |  | 1
Air Flue Gas (AFG) | GG | 3GG-F802A | ID FAN A REGULATOR COOLING FAN A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F802B | ID FAN A REGULATOR COOLING FAN B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F803A | ID FAN A BEARING COOLING FAN A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F803B | ID FAN A BEARING COOLING FAN B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F804A | ID FAN B REGULATOR COOLING FAN A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F804B | ID FAN B REGULATOR COOLING FAN B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F805A | ID FAN B BEARING COOLING FAN A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F805B | ID FAN B BEARING COOLING FAN B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F851 | ULTRASONIC BIRD CONTROL |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F853A | FGD BOOSTER FAN A COOLING FAN MOTOR VERTICAL A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F853B | FGD BOOSTER FAN A COOLING FAN MOTOR VERTICAL B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F853C | FGD BOOSTER FAN A COOLING FAN MOTOR VERTICAL C |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F853D | FGD BOOSTER FAN A COOLING FAN MOTOR VERTICAL D |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F854A | FGD BOOSTER FAN B COOLING FAN MOTOR VERTICAL A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F854B | FGD BOOSTER FAN B COOLING FAN MOTOR VERTICAL B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F854C | FGD BOOSTER FAN B COOLING FAN MOTOR VERTICAL C |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F854D | FGD BOOSTER FAN B COOLING FAN MOTOR VERTICAL D |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F865A | HIGH PRESSURE SEAL AIR FAN A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F865B | HIGH PRESSURE SEAL AIR FAN B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F870A | LOW PRESSURE SEAL AIR FAN A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F870B | LOW PRESSURE SEAL AIR FAN B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F875A | FGD BOOSTER FAN A COOLING FAN A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F875B | FGD BOOSTER FAN A COOLING FAN B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F880A | FGD BOOSTER FAN B COOLING FAN A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F880B | FGD BOOSTER FAN B COOLING FAN B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M865A | HIGH PRESSURE SEAL AIR FAN A MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M865B | HIGH PRESSURE SEAL AIR FAN B MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M870A | LOW PRESSURE SEAL AIR FAN A MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M870B | LOW PRESSURE SEAL AIR FAN B MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M875A | FGD BOOSTER FAN A COOLING FAN A MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M875B | FGD BOOSTER FAN A COOLING FAN B MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M877A | FGD BOOSTER FAN A LUBE OIL PUMP A MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M877B | FGD BOOSTER FAN A LUBE OIL PUMP B MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M878A | FGD BOOSTER FAN B LUBE OIL PUMP A MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M878B | FGD BOOSTER FAN B LUBE OIL PUMP B MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M880A | FGD BOOSTER FAN B COOLING FAN A MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-M880B | FGD BOOSTER FAN B COOLING FAN B MOTOR |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-P801A | ID FAN A OIL PUMP A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-P801B | ID FAN A OIL PUMP B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-P802A | ID FAN B OIL PUMP A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-P802B | ID FAN B OIL PUMP B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-P877A | FGD BOOSTER FAN A MOTOR LUBE OIL PUMP A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-P877B | FGD BOOSTER FAN A MOTOR LUBE OIL PUMP B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-P878A | FGD BOOSTER FAN B MOTOR LUBE OIL PUMP A |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-P878B | FGD BOOSTER FAN B MOTOR LUBE OIL PUMP B |  | NO TAG
Air Flue Gas (AFG) | GG | 3GG-F801A | INDUCED DRAFT FAN A | ID FAN A OUTL FLUE - GAS TEMP | 3GG-TE801A | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-200degC | 0 |  | Now: 150.5degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAnw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE9VVEwgRkxVRSBHQVMgVEVNUA
Air Flue Gas (AFG) | GG | 3GG-T801A | ID FAN A LUBE OIL SKID CONTROL PANEL | ID FAN A MN THRST - BRG NO.1 TEMP | 3GG-TE813A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pApw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIFRIUlNUIEJSRyBOTy4xIFRFTVAgQQ | 3GG-TE813C | 1
Air Flue Gas (AFG) | GG | 3GG-F801A | INDUCED DRAFT FAN A | ID FAN A MN THRST - BRG NO.2 TEMP | 3GG-TE814A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAqA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIFRIUlNUIEJSRyBOTy4xIFRFTVAgQg |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801A | INDUCED DRAFT FAN A | ID FAN A MN THRST - BRG NO.3 TEMP | 3GG-TE815A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAqQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIFRIUlNUIEJSRyBOTy4xIFRFTVAgQw |  | 1
Air Flue Gas (AFG) | GG | 3GG-T801A | ID FAN A LUBE OIL SKID CONTROL PANEL | ID FAN A MN ROLLING - BRG NO.1 TEMP | 3GG-TE816A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAoA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIFJPTExJTkcgQlJHIE5PLjEgVEVNUCBB | 3GG-TE816C | 1
Air Flue Gas (AFG) | GG | 3GG-F801A | INDUCED DRAFT FAN A | ID FAN A MN ROLLING - BRG NO.2 TEMP | 3GG-TE817A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAoQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIFJPTExJTkcgQlJHIE5PLjEgVEVNUCBC |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801A | INDUCED DRAFT FAN A | ID FAN A MN ROLLING - BRG NO.3 TEMP | 3GG-TE818A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAog0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIFJPTExJTkcgQlJHIE5PLjEgVEVNUCBD |  | 1
Air Flue Gas (AFG) | GG | 3GG-T801A | ID FAN A LUBE OIL SKID CONTROL PANEL | ID FAN A MN ROLLING - BRG NO.4 TEMP | 3GG-TE819A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAow0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIFJPTExJTkcgQlJHIE5PLjIgVEVNUCBB | 3GG-TE819C | 1
Air Flue Gas (AFG) | GG | 3GG-F801A | INDUCED DRAFT FAN A | ID FAN A MN ROLLING - BRG NO.5 TEMP | 3GG-TE820A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pApA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIFJPTExJTkcgQlJHIE5PLjIgVEVNUCBC |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801A | INDUCED DRAFT FAN A | ID FAN A MN ROLLING - BRG NO.6 TEMP | 3GG-TE821A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pApQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIFJPTExJTkcgQlJHIE5PLjIgVEVNUCBD |  | 1
Air Flue Gas (AFG) | GG | 3GG-T801A | ID FAN A LUBE OIL SKID CONTROL PANEL | ID FAN A HORIZ VIBN | 3GG-VE801A | 1 | mm/s |  | -999999 | -999999 |  | 0 | 0 | 2025-05-04 | 11 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAlQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIEhPUklaIFZJQk4 |  | 1
Air Flue Gas (AFG) | GG | 3GG-T801A | ID FAN A LUBE OIL SKID CONTROL PANEL | ID FAN A VERT VIBN | 3GG-VE802A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 2025-05-04 | 11 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAqw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIFZFUlQgVklCTg |  | 1
Air Flue Gas (AFG) | GG | 3GG-T801A | ID FAN A LUBE OIL SKID CONTROL PANEL | ID FAN A SUR PROT DP | 3GG-DPIX801A | 1 |  |  | -999999 |  |  | 0 |  | 40 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pApg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIFNVUiBQUk9UIERQ |  | 1
Air Flue Gas (AFG) | GG | 3GG-T801A | ID FAN A LUBE OIL SKID CONTROL PANEL | ID FAN A INL FLUE GAS PRESS | 3GG-PIX801A | 1 | [8 empty] | -60 - 0 mbar |  |  | Now : -22 mbar |  | F1DPw1kUu10ziUaXEx2rIyo4pAlg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIElOTCBGTFVFIEdBUyBQUkVTUw |  | 1
Air Flue Gas (AFG) | GG | 3GG-T801A | ID FAN A LUBE OIL SKID CONTROL PANEL | ID FAN A OUTL FLUE GAS PRESS | 3GG-PIX802A | 1 | [8 empty] | -10 - 10 mbar |  |  | Now : 2.3 mbar |  | F1DPw1kUu10ziUaXEx2rIyo4pAng0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE9VVEwgRkxVRSBHQVMgUFJFU1M |  | 1
Air Flue Gas (AFG) | GG | 3GG-T801A | ID FAN A LUBE OIL SKID CONTROL PANEL | ID FAN A OUTL FLUE GAS TEMP | 3GG-TE801A | 1 |  |  | -999999 |  |  |  |  | 999999 | 0-200degC |  |  | Now : 139.5 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAnw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE9VVEwgRkxVRSBHQVMgVEVNUA |  | 1
Air Flue Gas (AFG) | GG | 3GG-T801A | ID FAN A LUBE OIL SKID CONTROL PANEL | ID FAN A OIL TK TEMP | 3GG-TE830A | 1 |  |  | 25 |  |  | 0 |  | 999999 | 0-100degC | 0 |  | Now : 59.5 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAnQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE9JTCBUSyBURU1Q |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810A | ID FAN A MOTOR | ID FAN A MTR CUR | 3GG-F801A-A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAmQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE1UUiBDVVI |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810A | ID FAN A MOTOR | ID FAN A MTR BRG NO.1 TEMP | 3GG-TE811A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAlw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE1UUiBCUkcgTk8uMSBURU1Q |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810A | ID FAN A MOTOR | ID FAN A MTR BRG NO.2 TEMP | 3GG-TE812A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE1UUiBCUkcgTk8uMiBURU1Q |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810A | ID FAN A MOTOR | STAT WDG TEMP U | 3GG-TE822A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE1UUiBTVEFUIFdERyBURU1QIFU |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810A | ID FAN A MOTOR | STAT WDG TEMP U | 3GG-TE823A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE1UUiBTVEFUIFdERyBURU1QIFU
Air Flue Gas (AFG) | GG | 3GG-M810A | ID FAN A MOTOR | STAT WDG TEMP V | 3GG-TE824A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE1UUiBTVEFUIFdERyBURU1QIFY |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810A | ID FAN A MOTOR | STAT WDG TEMP V | 3GG-TE825A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAmw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE1UUiBTVEFUIFdERyBURU1QIFY
Air Flue Gas (AFG) | GG | 3GG-M810A | ID FAN A MOTOR | STAT WDG TEMP W | 3GG-TE826A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAnA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE1UUiBTVEFUIFdERyBURU1QIFc |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810A | ID FAN A MOTOR | STAT WDG TEMP W | 3GG-TE827A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 110 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAnA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBBIE1UUiBTVEFUIFdERyBURU1QIFc
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B OUTL FLUE - GAS TEMP | 3GG-TE801B | 1 |  |  | -999999 |  |  | 0 |  | 999999 | 0-200degC | 0 |  | Now: 150.5degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAtg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE9VVEwgRkxVRSBHQVMgVEVNUA |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B MN THRST - BRG NO.1 TEMP | 3GG-TE813B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAvg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIFRIUlNUIEJSRyBOTy4xIFRFTVAgQQ |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B MN THRST - BRG NO.2 TEMP | 3GG-TE814B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAvw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIFRIUlNUIEJSRyBOTy4xIFRFTVAgQg | 3GG-TE814C | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B MN THRST - BRG NO.3 TEMP | 3GG-TE815B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAwA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIFRIUlNUIEJSRyBOTy4xIFRFTVAgQw |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B MN ROLLING - BRG NO.1 TEMP | 3GG-TE816B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAtw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIFJPTExJTkcgQlJHIE5PLjEgVEVNUCBB |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B MN ROLLING - BRG NO.2 TEMP | 3GG-TE817B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAuA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIFJPTExJTkcgQlJHIE5PLjEgVEVNUCBC | 3GG-TE817C | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B MN ROLLING - BRG NO.3 TEMP | 3GG-TE818B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAuQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIFJPTExJTkcgQlJHIE5PLjEgVEVNUCBD |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B MN ROLLING - BRG NO.4 TEMP | 3GG-TE819B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAug0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIFJPTExJTkcgQlJHIE5PLjIgVEVNUCBB |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B MN ROLLING - BRG NO.5 TEMP | 3GG-TE820B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 110 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAuw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIFJPTExJTkcgQlJHIE5PLjIgVEVNUCBC | 3GG-TE820C | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B MN ROLLING - BRG NO.6 TEMP | 3GG-TE821B | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAvA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIFJPTExJTkcgQlJHIE5PLjIgVEVNUCBD |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B HORIZ VIBN | 3GG-VE801B | 1 | mm/s |  | -999999 | -999999 |  | 0 | 0 | 2025-05-04 | 11 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pArA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIEhPUklaIFZJQk4 |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B VERT VIBN | 3GG-VE802B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 2025-05-04 | 11 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAwg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIFZFUlQgVklCTg |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | ID FAN B SUR PROT DP | 3GG-DPIX801B | 1 |  |  | -999999 |  |  | 0 |  | 40 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAvQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIFNVUiBQUk9UIERQ |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | INL FLUE GAS PRESS | 3GG-PIX801B | 1 | [8 empty] | -60 - 0 mbar |  |  | Now : -22 mbar |  | F1DPw1kUu10ziUaXEx2rIyo4pArQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIElOTCBGTFVFIEdBUyBQUkVTUw |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | OUTL FLUE GAS PRESS | 3GG-PIX802B | 1 | [8 empty] | -10 - 10 mbar |  |  | Now : 2.3 mbar |  | F1DPw1kUu10ziUaXEx2rIyo4pAtQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE9VVEwgRkxVRSBHQVMgUFJFU1M |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | OUTL FLUE GAS TEMP | 3GG-TE801B | 1 | [8 empty] | 0-200degC |  |  | Now : 139.5 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAtg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE9VVEwgRkxVRSBHQVMgVEVNUA |  | 1
Air Flue Gas (AFG) | GG | 3GG-F801B | INDUCED DRAFT FAN B | OIL TK TEMP | 3GG-TE830B | 1 |  |  | 25 |  |  | 0 |  | 999999 | 0-100degC | 0 |  | Now : 59.5 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAtA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE9JTCBUSyBURU1Q |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810B | ID FAN B MOTOR | ID FAN B MTR CUR | 3GG-F801B-A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAsA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE1UUiBDVVI |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810B | ID FAN B MOTOR | MTR BRG NO.1 TEMP | 3GG-TE811B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 70 | 80 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pArg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE1UUiBCUkcgTk8uMSBURU1Q |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810B | ID FAN B MOTOR | MTR BRG NO.2 TEMP | 3GG-TE812B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 70 | 80 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pArw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE1UUiBCUkcgTk8uMiBURU1Q |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810B | ID FAN B MOTOR | MTR STAT WDG TEMP U | 3GG-TE822B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAsQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE1UUiBTVEFUIFdERyBURU1QIFU |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810B | ID FAN B MOTOR | MTR STAT WDG TEMP U | 3GG-TE823B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAsQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE1UUiBTVEFUIFdERyBURU1QIFU
Air Flue Gas (AFG) | GG | 3GG-M810B | ID FAN B MOTOR | MTR STAT WDG TEMP V | 3GG-TE824B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAsg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE1UUiBTVEFUIFdERyBURU1QIFY |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810B | ID FAN B MOTOR | MTR STAT WDG TEMP V | 3GG-TE825B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAsg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE1UUiBTVEFUIFdERyBURU1QIFY
Air Flue Gas (AFG) | GG | 3GG-M810B | ID FAN B MOTOR | MTR STAT WDG TEMP W | 3GG-TE826B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAsw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE1UUiBTVEFUIFdERyBURU1QIFc |  | 1
Air Flue Gas (AFG) | GG | 3GG-M810B | ID FAN B MOTOR | MTR STAT WDG TEMP W | 3GG-TE827B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAsw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklEIEZBTiBCIE1UUiBTVEFUIFdERyBURU1QIFc
Air Flue Gas (AFG) | GG | 3GG-F851 | FGD BOOSTER FAN A | BSTR FAN A/B INL PRESS | 3GG-PIX851A | 1 |  |  | -5 | -8 |  |  |  | 4 | 999999 |  |  | Now : -1.53degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAaQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEvQiBJTkwgUFJFU1M | 3GG-PIX851C | 1
Air Flue Gas (AFG) | GG | 3GG-T877 | FGD BOOSTER FAN A MOTOR LUBE OIL TANK | BSTR FAN A ROLLING BRG NO.1 TEMP A | 3GG-TE968A | 1 |  |  | -999999 | -999999 |  |  |  | 90 | 100 |  |  | Now : 45.8 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAXgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgUk9MTElORyBCUkcgTk8uMSBURU1QIEE |  | 1
Air Flue Gas (AFG) | GG | 3GG-T877 | FGD BOOSTER FAN A MOTOR LUBE OIL TANK | BSTR FAN A ROLLING BRG NO.1 TEMP B | 3GG-TE968B | 1 |  |  | -999999 | -999999 |  |  |  | 90 | 100 |  |  | Now : 45.8 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAXwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgUk9MTElORyBCUkcgTk8uMSBURU1QIEI |  | 1
Air Flue Gas (AFG) | GG | 3GG-T877 | FGD BOOSTER FAN A MOTOR LUBE OIL TANK | BSTR FAN A ROLLING BRG NO.1 TEMP C | 3GG-TE968C | 1 |  |  | -999999 | -999999 |  |  |  | 90 | 100 |  |  | Now : 45.8 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAYAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgUk9MTElORyBCUkcgTk8uMSBURU1QIEM |  | 1
Air Flue Gas (AFG) | GG | 3GG-F854 | FGD BOOSTER FAN A | BSTR FAN A THRST BRG NO.1 TEMP A | 3GG-TE969A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAYQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgVEhSU1QgQlJHIE5PLjEgVEVNUCBB |  | 1
Air Flue Gas (AFG) | GG |  |  | BSTR FAN A THRST BRG NO.1 TEMP B | 3GG-TE969B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAYgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgVEhSU1QgQlJHIE5PLjEgVEVNUCBC
Air Flue Gas (AFG) | GG |  |  | BSTR FAN A THRST BRG NO.1 TEMP C | 3GG-TE969C | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAYwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgVEhSU1QgQlJHIE5PLjEgVEVNUCBD
Air Flue Gas (AFG) | GG | 3GG-F855 | FGD BOOSTER FAN A | BSTR FAN A THRST BRG NO.2 TEMP A | 3GG-TE970A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAZAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgVEhSU1QgQlJHIE5PLjIgVEVNUCBB |  | 1
Air Flue Gas (AFG) | GG |  |  | BSTR FAN A THRST BRG NO.2 TEMP B | 3GG-TE970B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAZQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgVEhSU1QgQlJHIE5PLjIgVEVNUCBC
Air Flue Gas (AFG) | GG |  |  | BSTR FAN A THRST BRG NO.2 TEMP C | 3GG-TE970C | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAZgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgVEhSU1QgQlJHIE5PLjIgVEVNUCBD
Air Flue Gas (AFG) | GG | 3GG-F856 | FGD BOOSTER FAN A | HORIZ VIBN | 3GG-VE851 | 1 | mm |  | -999999 | -999999 |  | 0 | 0 | 2025-06-04 | 2025-01-07 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAVgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgSE9SSVogVklCTg |  | 1
Air Flue Gas (AFG) | GG | 3GG-F857 | FGD BOOSTER FAN A | VERT VIBN | 3GG-VE852 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 2025-06-04 | 2025-01-07 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAZwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgVkVSVCBWSUJO |  | 1
Air Flue Gas (AFG) | GG | 3GG-F858 | FGD BOOSTER FAN A | OUTL DMPR DP | 3GG-DPIX852 | 1 | bar |  | 5 |  |  | 35 |  | 999999 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAXQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgT1VUTCBETVBSIERQ |  | 1
Air Flue Gas (AFG) | GG | 3GG-F859 | FGD BOOSTER FAN A | INL DMPR DP | 3GG-DPIX853 | 1 |  |  | 5 |  |  | 35 |  | 999999 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAVwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgSU5MIERNUFIgRFA |  | 1
Air Flue Gas (AFG) | GG | 3GG-F860 | FGD BOOSTER FAN A | BSTR FAN A FLW | 3GG-FIX851 | 1 | [8 empty] | 0-60mbar |  |  | Now : 2.8 mbarg |  | F1DPw1kUu10ziUaXEx2rIyo4pAVQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgRkxX |  | 1
Air Flue Gas (AFG) | GG | 3GG-M852 | FGD BOOSTER FAN A MOTOR | BSTR FAN A CUR | 3GG-F851-A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAUwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgQ1VS |  | 1
Air Flue Gas (AFG) | GG | 3GG-M853 | FGD BOOSTER FAN A MOTOR | BSTR FAN A MTR BRG NO.1 TEMP | 3GG-TE951A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAWAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgTVRSIEJSRyBOTy4xIFRFTVA |  | 1
Air Flue Gas (AFG) | GG | 3GG-M854 | FGD BOOSTER FAN A MOTOR | BSTR FAN A MTR BRG NO.2 TEMP | 3GG-TE952A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAWQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgTVRSIEJSRyBOTy4yIFRFTVA |  | 1
Air Flue Gas (AFG) | GG | 3GG-M855 | FGD BOOSTER FAN A MOTOR | MTR STAT WDG TEMP U | 3GG-TE953A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 115 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAWgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgTVRSIFNUQVQgV0RHIFRFTVAgVQ |  | 1
Air Flue Gas (AFG) | GG | 3GG-M856 | FGD BOOSTER FAN A MOTOR | MTR STAT WDG TEMP U | 3GG-TE953B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 115 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAWgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgTVRSIFNUQVQgV0RHIFRFTVAgVQ
Air Flue Gas (AFG) | GG | 3GG-M857 | FGD BOOSTER FAN A MOTOR | MTR STAT WDG TEMP V | 3GG-TE954A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 115 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAWwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgTVRSIFNUQVQgV0RHIFRFTVAgVg |  | 1
Air Flue Gas (AFG) | GG | 3GG-M858 | FGD BOOSTER FAN A MOTOR | MTR STAT WDG TEMP V | 3GG-TE954B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 115 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAWwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgTVRSIFNUQVQgV0RHIFRFTVAgVg
Air Flue Gas (AFG) | GG | 3GG-M859 | FGD BOOSTER FAN A MOTOR | MTR STAT WDG TEMP W | 3GG-TE955A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 115 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAXAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgTVRSIFNUQVQgV0RHIFRFTVAgVw |  | 1
Air Flue Gas (AFG) | GG | 3GG-M860 | FGD BOOSTER FAN A MOTOR | MTR STAT WDG TEMP W | 3GG-TE955B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 115 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAXAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEEgTVRSIFNUQVQgV0RHIFRFTVAgVw
Air Flue Gas (AFG) | GG | 3GG-F854 | FGD BOOSTER FAN B | ROLLING BRG NO.1 TEMP | 3GG-TE986A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAegsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgUk9MTElORyBCUkcgTk8uMSBURU1QIEE |  | 1
Air Flue Gas (AFG) | GG |  |  | BSTR FAN B ROLLING BRG NO.1 TEMP B | 3GG-TE986B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAewsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgUk9MTElORyBCUkcgTk8uMSBURU1QIEI
Air Flue Gas (AFG) | GG |  |  | BSTR FAN B ROLLING BRG NO.1 TEMP C | 3GG-TE986C | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgUk9MTElORyBCUkcgTk8uMSBURU1QIEM
Air Flue Gas (AFG) | GG | 3GG-F855 | FGD BOOSTER FAN B | THRST BRG NO.1 TEMP | 3GG-TE987A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgVEhSU1QgQlJHIE5PLjEgVEVNUCBB |  | 1
Air Flue Gas (AFG) | GG |  |  | BSTR FAN B THRST BRG NO.1 TEMP B | 3GG-TE987B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgVEhSU1QgQlJHIE5PLjEgVEVNUCBC
Air Flue Gas (AFG) | GG |  |  | BSTR FAN B THRST BRG NO.1 TEMP C | 3GG-TE987C | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgVEhSU1QgQlJHIE5PLjEgVEVNUCBD
Air Flue Gas (AFG) | GG | 3GG-F856 | FGD BOOSTER FAN B | THRST BRG NO.2 TEMP | 3GG-TE988A | 1 |  |  | -999999 | -999999 |  |  |  | 90 | 100 |  |  | Now: 49.5 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAgAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgVEhSU1QgQlJHIE5PLjIgVEVNUCBB |  | 1
Air Flue Gas (AFG) | GG |  |  | BSTR FAN B THRST BRG NO.2 TEMP B | 3GG-TE988B | 1 |  |  | -999999 | -999999 |  |  |  | 90 | 100 |  |  | Now: 49.5 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAgQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgVEhSU1QgQlJHIE5PLjIgVEVNUCBC
Air Flue Gas (AFG) | GG |  |  | BSTR FAN B THRST BRG NO.2 TEMP C | 3GG-TE988C | 1 |  |  | -999999 | -999999 |  |  |  | 90 | 100 |  |  | Now: 49.5 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAggsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgVEhSU1QgQlJHIE5PLjIgVEVNUCBD
Air Flue Gas (AFG) | GG | 3GG-F857 | FGD BOOSTER FAN B | HORIZ VIBN | 3GG-VE853 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 2025-06-04 | 2025-01-07 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAcgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgSE9SSVogVklCTg |  | 1
Air Flue Gas (AFG) | GG | 3GG-F858 | FGD BOOSTER FAN B | VERT VIBN | 3GG-VE854 | 1 | mm |  | -999999 | -999999 |  | 0 | 0 | 2025-06-04 | 2025-01-07 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAgwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgVkVSVCBWSUJO |  | 1
Air Flue Gas (AFG) | GG | 3GG-F859 | FGD BOOSTER FAN B | OUTL DMPR DP | 3GG-DPIX854 | 1 |  |  | 5 |  |  | 35 |  | 999999 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAeQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgT1VUTCBETVBSIERQ |  | 1
Air Flue Gas (AFG) | GG | 3GG-F860 | FGD BOOSTER FAN B | INL DMPR DP | 3GG-DPIX855 | 1 |  |  | 5 |  |  | 35 |  | 999999 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAcwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgSU5MIERNUFIgRFA |  | 1
Air Flue Gas (AFG) | GG | 3GG-F861 | FGD BOOSTER FAN B | FLW | 3GG-FIX852 | 1 | [8 empty] | 0-60mbar |  |  | Now : 2.8 mbarg |  | F1DPw1kUu10ziUaXEx2rIyo4pAcQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgRkxX |  | 1
Air Flue Gas (AFG) | GG | 3GG-M853 | FGD BOOSTER FAN B MOTOR | CURRENT | 3GG-F852-A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAbwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgQ1VS |  | 1
Air Flue Gas (AFG) | GG | 3GG-M854 | FGD BOOSTER FAN B MOTOR | MTR BRG NO.1 TEMP | 3GG-TE951B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAdAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgTVRSIEJSRyBOTy4xIFRFTVA |  | 1
Air Flue Gas (AFG) | GG | 3GG-M855 | FGD BOOSTER FAN B MOTOR | MTR BRG NO.2 TEMP | 3GG-TE952B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAdQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgTVRSIEJSRyBOTy4yIFRFTVA |  | 1
Air Flue Gas (AFG) | GG | 3GG-M856 | FGD BOOSTER FAN B MOTOR | MTR STAT WDG TEMP U | 3GG-TE983A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAdgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgTVRSIFNUQVQgV0RHIFRFTVAgVQ |  | 1
Air Flue Gas (AFG) | GG | 3GG-M857 | FGD BOOSTER FAN B MOTOR | MTR STAT WDG TEMP U | 3GG-TE983B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAdgsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgTVRSIFNUQVQgV0RHIFRFTVAgVQ
Air Flue Gas (AFG) | GG | 3GG-M858 | FGD BOOSTER FAN B MOTOR | MTR STAT WDG TEMP V | 3GG-TE984A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAdwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgTVRSIFNUQVQgV0RHIFRFTVAgVg |  | 1
Air Flue Gas (AFG) | GG | 3GG-M859 | FGD BOOSTER FAN B MOTOR | MTR STAT WDG TEMP V | 3GG-TE984B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAdwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgTVRSIFNUQVQgV0RHIFRFTVAgVg
Air Flue Gas (AFG) | GG | 3GG-M860 | FGD BOOSTER FAN B MOTOR | MTR STAT WDG TEMP W | 3GG-TE985A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAeAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgTVRSIFNUQVQgV0RHIFRFTVAgVw |  | 1
Air Flue Gas (AFG) | GG | 3GG-M861 | FGD BOOSTER FAN B MOTOR | MTR STAT WDG TEMP W | 3GG-TE985B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAeAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgTVRSIFNUQVQgV0RHIFRFTVAgVw
Generator (GEN) | GMC | 3GMC-Z002 | GENERATOR MAIN CIRCUIT BREAKER | GENERATOR MW | 3GMC-HSIG026 | 1 |  |  | -999999 |  |  | 0 |  | 999999 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAMg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkdFTkVSQVRPUiBNVw |  | 1
Turbine (TUR) | GSS | 3GSS-M011A | GLAND STEAM EXHAUSTER A MOTOR
Turbine (TUR) | GSS | 3GSS-M011B | GLAND STEAM EXHAUSTER B MOTOR
Generator (GEN) | H2 | NOT ELIGIBLE | Generator Hydrogen System
Turbine (TUR) | HPB | NOT ELIGIBLE | HP Turbine Bypass System
Boiler (BOL) | HRH | NOT ELIGIBLE | Hot Reheat Steam System |  | A | [14 empty] | B
Boiler (BOL) | HRH | NOT ELIGIBLE | RSV A SERVO CURRENT | RSV A SERVO CURRENT | 3HRH-HV021A-F
Boiler (BOL) | HRH | NOT ELIGIBLE | RSV A SERVO CURRENT | RSV B SERVO CURRENT | 3HRH-HV021B-F
Boiler (BOL) | HRH | NOT ELIGIBLE | ICV A SERVO CURRENT | ICV A SERVO CURRENT | 3HRH-HV022A-F
Boiler (BOL) | HRH | NOT ELIGIBLE | ICV A SERVO CURRENT | ICV B SERVO CURRENT | 3HRH-HV022B-F
SAC IAC (SAC) | IA | NOT ELIGIBLE | Instrument Air System
Feedwater (FW) | LOM | 3LOM-M330 | MBFP AUXILIARY OIL PUMP MOTOR
Feedwater (FW) | LOM | 3LOM-P310 | MBFP LUBE OIL PUMP | MBFP LUB OIL PRESS A | 3LOM-PIX301 | 1 |  |  | 0.8 |  |  |  |  | 999999 | 0-6barg |  |  | Now: -0.005barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAOA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTFVCIE9JTCBQUkVTUyBB |  | 1
Feedwater (FW) | LOM | 3LOM-P311 | MBFP LUBE OIL PUMP | MBFP LUB OIL PRESS B | 3LOM-PIX302 | 1 |  |  | 0.8 |  |  |  |  | 999999 | 0-6barg |  |  | Now: -0.005barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAOQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTFVCIE9JTCBQUkVTUyBC |  | 1
Feedwater (FW) | LOM | 3LOM-P312 | MBFP LUBE OIL PUMP | MBFP LUB OIL PRESS C | 3LOM-PIX303 | 1 |  |  | 0.8 |  |  |  |  | 999999 | 0-6barg |  |  | Now: -0.005barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAOg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTFVCIE9JTCBQUkVTUyBD |  | 1
Feedwater (FW) | LOM | 3LOM-P313 | MBFP LUBE OIL PUMP | MBFP OPRN OIL PRESS | 3LOM-PG101
Feedwater (FW) | LOM | 3LOM-P314 | MBFP LUBE OIL PUMP | MBFP LUBE OIL PRESS | 3LOM-PG102 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pANw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTFVCIE9JTCBQUkVTUw |  | 1
Feedwater (FW) | LOM | 3LOM-P330 | MBFP AUXILIARY OIL PUMP
Feedwater (FW) | LOM | 3LOM-P370 | MBFP WORKING OIL PUMP
Turbine (TUR) | LOS | 3LOS-M010A | MAIN OIL PUMP A MOTOR
Turbine (TUR) | LOS | 3LOS-M010B | MAIN OIL PUMP B MOTOR
Turbine (TUR) | LOS | 3LOS-M020A | MAIN OIL TANK VAPOUR EXTRACTOR A MOTOR
Turbine (TUR) | LOS | 3LOS-M020B | MAIN OIL TANK VAPOUR EXTRACTOR B MOTOR
Turbine (TUR) | LOS | 3LOS-M050 | EMERGENCY OIL PUMP MOTOR
Turbine (TUR) | LOS | 3LOS-M060 | MAIN OIL TANK TRANSFER PUMP MOTOR
Turbine (TUR) | LOS | 3LOS-M080 | MAIN OIL CONDITIONER FILTER PUMP MOTOR
Turbine (TUR) | LOS | 3LOS-P010A | MAIN OIL PUMP A | MOP A OUTL PRESS | 3LOS-PG002A
Turbine (TUR) | LOS | 3LOS-P010B | MAIN OIL PUMP B | MOP B OUTL PRESS | 3LOS-PG002B
Turbine (TUR) | LOS | 3LOS-P050 | EMERGENCY OIL PUMP
Turbine (TUR) | LOS | 3LOS-P060 | MAIN OIL TANK TRANSFER PUMP
Turbine (TUR) | LOS | 3LOS-P080 | MAIN OIL CONDITIONER FILTER PUMP
Feedwater (FW) | LOT | 3LOT-M010A | BFPT A MAIN OIL PUMP A MOTOR
Feedwater (FW) | LOT | 3LOT-M010B | BFPT B MAIN OIL PUMP A MOTOR
Feedwater (FW) | LOT | 3LOT-M020A | BFPT A MAIN OIL PUMP B MOTOR
Feedwater (FW) | LOT | 3LOT-M020B | BFPT B MAIN OIL PUMP B MOTOR
Feedwater (FW) | LOT | 3LOT-M050A | BFPT A EMERGENCY OIL PUMP MOTOR
Feedwater (FW) | LOT | 3LOT-M050B | BFPT B EMERGENCY OIL PUMP MOTOR
Feedwater (FW) | LOT | 3LOT-M080A | BFPT A OIL CONDITIONER FILTER PUMP MOTOR
Feedwater (FW) | LOT | 3LOT-M080B | BFPT B OIL CONDITIONER FILTER PUMP MOTOR
Feedwater (FW) | LOT | 3LOT-M120A | BFPT A MAIN OIL TANK VAPOUR EXTRACTOR MOTOR
Feedwater (FW) | LOT | 3LOT-M120B | BFPT B MAIN OIL TANK VAPOUR EXTRACTOR MOTOR
Feedwater (FW) | LOT | 3LOT-ME120 | BFPT OIL TANK OIL SEPARATOR
Feedwater (FW) | LOT | 3LOT-P010A | BFPT A MAIN OIL PUMP A |  | NON DCS
Feedwater (FW) | LOT | 3LOT-P010B | BFPT B MAIN OIL PUMP A |  | NON DCS
Feedwater (FW) | LOT | 3LOT-P020A | BFPT A MAIN OIL PUMP B |  | NON DCS
Feedwater (FW) | LOT | 3LOT-P020B | BFPT B MAIN OIL PUMP B |  | NON DCS
Feedwater (FW) | LOT | 3LOT-P050A | BFPT A EMERGENCY OIL PUMP
Feedwater (FW) | LOT | 3LOT-P050B | BFPT B EMERGENCY OIL PUMP
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP
Feedwater (FW) | LOT | 3LOT-P080B | BFPT B OIL CONDITIONER FILTER PUMP
Turbine (TUR) | LPB | NOT ELIGIBLE | LP Turbine Bypass System
FGD Support (SUP) | LSH | 00LSH-F901 | LIMESTONE SILO DUST COLLECTOR FAN
FGD Support (SUP) | LSH | 00LSH-M851 | LIMESTONE VIBRATING FEEDER MOTOR
FGD Support (SUP) | LSH | 00LSH-M852 | LIMESTONE BUCKET ELEVATOR MOTOR
FGD Support (SUP) | LSH | 00LSH-M901 | LIMESTONE PRE-CRUSHER DUST COLLECTOR FAN MOTOR
FGD Support (SUP) | LSH | 00LSH-M853A | LIMESTONE PRE-CRUSHER MOTOR | LMST PRE-CRSHR CUR | 00LSH-CR853-A |  |  |  | 0 |  |  | 0 |  | 999999 |  | 0
FGD Support (SUP) | LSH | 00LSH-M853A | LIMESTONE PRE-CRUSHER MOTOR | LMST PRE-CRSHR RTR SPD | 00LSH-SE853 |  |  |  | 753 |  |  | 0 |  | 999999 |  | 0
FGD Support (SUP) | LSH | 00LSH-M853A | LIMESTONE PRE-CRUSHER MOTOR | LMST PRE-CRSHR NO.1 BRG TEMP | 00LSH-TE853 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 70 | 80 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAAAIAAAS1RKQi1LSTAwLVBJMVxUSkIxLkNSVVNIRVIgQSBJTkJPQVJEIEJFQVJJTkcgVEVNUA
FGD Support (SUP) | LSH | 00LSH-M853A | LIMESTONE PRE-CRUSHER MOTOR | LMST PRE-CRSHR NO.2 BRG TEMP | 00LSH-TE854 | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 70 | 80 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pABAIAAAS1RKQi1LSTAwLVBJMVxUSkIxLkNSVVNIRVIgQSBPVVRCT0FSRCBCRUFSSU5HIFRFTVA
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | HPT 1ST STG PRESS | 3MT-PIX001A | 1 |  |  | -999999 | -999999 |  | 0 |  | 999999 | 999999 |  |  | Now: 85.8 Barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAbg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCAxU1QgU1RHIFBSRVNT |  | 1
Turbine (TUR) | MT | 3MT-ST011 | HP TURBINE | HPT 1ST STG PRESS B | 3MT-PIX001B | 1 |  |  | -999999 | -999999 |  | 0 |  | 999999 | 999999 | 0 |  | Now: 85.8 Barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAbw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCAxU1QgU1RHIFBSRVNTIEI |  | 1
Turbine (TUR) | MT | 3MT-ST012 | HP TURBINE | HPT 1ST STG PRESS C | 3MT-PIX001C | 1 |  |  | -999999 | -999999 |  | 0 |  | 999999 | 999999 | 0 |  | Now: 85.8 Barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAcA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCAxU1QgU1RHIFBSRVNTIEM |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | HPT 1ST STAGE PRESS | 3MT-PIX001B-N | 1 |  |  | -999999 | -999999 |  |  |  | 999999 | 999999 |  |  | Now: 85.8 Barg |  | F1DPw1kUu10ziUaXEx2rIyo4pAaQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCAxU1QgU1RBR0UgUFJFU1M |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | HPT 1ST STG INR MET TEMP | 3MT-TE001 | 1 |  |  | -999999 | -999999 |  |  |  | 999999 | 0-600 degC |  |  | Now: 473.5degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAbA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCAxU1QgU1RHIElOUiBNRVQgVEVNUA |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | HPT 1ST STAGE OUT MTL TEMP | 3MT-TE002 | 1 |  |  | -999999 | -999999 |  |  |  | 999999 | 0-600 degC |  |  | Now: 473.5degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAaA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCAxU1QgU1RBR0UgT1VUIE1UTCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | HPT EXTR LWR INR MET TEMP | 3MT-TE003 | 1 |  |  | -999999 | -999999 |  |  |  | 999999 | 0-600 degC |  |  | Now: 415.3 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAhQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCBFWFRSIExXUiBJTlIgTUVUIFRFTVA |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | HPT EXTR UPR INR MET TEMP | 3MT-TE004 | 1 |  |  | -999999 | -999999 |  |  |  | 999999 | 0-600 degC |  |  | Now: 421.3 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAhg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCBFWFRSIFVQUiBJTlIgTUVUIFRFTVA |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | HPT EXH LWR INR MET TEMP | 3MT-TE005 | 1 |  |  | -999999 | -999999 |  |  |  | 999999 | 0-600 degC |  |  | Now: 328 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAfw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCBFWEggTFdSIElOUiBNRVQgVEVNUA |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | HPT EXH UPR INR MET TEMP | 3MT-TE006 | 1 |  |  | -999999 | -999999 |  |  |  | 999999 | 0-600 degC |  |  | Now: 328 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAgw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCBFWEggVVBSIElOUiBNRVQgVEVNUA |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | BRG 1 VIBN X | 3MT-VE001A-N | 1 | [5 empty] | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAKwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAxIFZJQk4gWA |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | BRG 1 VIBN Y | 3MT-VE001B-N | 1 | µmpp |  |  |  |  | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pALAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAxIFZJQk4gWQ |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | BRG 2 VIBN X | 3MT-VE002A-N | 1 | [5 empty] | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAMwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAyIFZJQk4gWA |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | BRG 2 VIBN Y | 3MT-VE002B-N | 1 | [5 empty] | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pANAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAyIFZJQk4gWQ |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | BRG 1 MET TEMP | 3MT-TE021 | 1 |  |  | -999999 |  |  | 0 |  | 115 | 0-150 degC | 0 |  | Now: 86 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAKQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAxIE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | BRG 2 MET TEMP | 3MT-TE022 | 1 |  |  | -999999 |  |  | 0 |  | 115 | 0-150 degC | 0 |  | Now: 92 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAMQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAyIE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | HPT DIFF EXP | 3MT-ZE002 | 1 |  |  | 2025-07-02 |  |  | 0 |  | 2025-03-22 | 0-25mm | 0 |  | Now: 12 mm |  | F1DPw1kUu10ziUaXEx2rIyo4pAfg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCBESUZGIEVYUA |  | 1
Turbine (TUR) | MT | 3MT-ST010 | HP TURBINE | HPT SHL EXP | 3MT-ZE003 | 1 | [8 empty] | 0-70mm |  |  | Now: 49.9 mm |  | F1DPw1kUu10ziUaXEx2rIyo4pAiA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkhQVCBTSEwgRVhQ |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | IPT RHT BWL PRESS | 3MT-PIX002 | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA2Q0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklQVCBSSFQgQldMIFBSRVNT |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | TURBINE ZERO SPD | 3MT-SE001G | [14 empty] | 0
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | IPT RH BWL INR MET TEMP | 3MT-TE007 | 1 | [8 empty] | 0-600 degC |  |  | Now: 534 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA1g0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklQVCBSSCBCV0wgSU5SIE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | IPT RH BWL OUT MET TEMP | 3MT-TE008 | 1 | [8 empty] | 0-600 degC |  |  | Now: 534 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA2A0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklQVCBSSCBCV0wgT1VUIE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | IPT EXTR LWR INR MET TEMP-TURB SIDE | 3MT-TE009A | 1 | [8 empty] | 0-600 degC |  |  | Now: 458 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA0Q0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklQVCBFWFRSIExXUiBJTlIgTUVUIFRFTVAtVFVSQiBTSURF |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | IPT EXTR LWR INR MET TEMP-GEN SIDE | 3MT-TE009B | 1 | [8 empty] | 0-600 degC |  |  | Now: 458 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA0A0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklQVCBFWFRSIExXUiBJTlIgTUVUIFRFTVAtR0VOIFNJREU |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | IPT EXTR UPR INR MET TEMP-TURB SIDE | 3MT-TE010A | 1 | [8 empty] | 0-600 degC |  |  | Now: 458 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA0Q0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklQVCBFWFRSIExXUiBJTlIgTUVUIFRFTVAtVFVSQiBTSURF |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | IPT EXTR UPR INR MET TEMP-GEN SIDE | 3MT-TE010B | 1 | [8 empty] | 0-600 degC |  |  | Now: 458 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pA0g0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklQVCBFWFRSIFVQUiBJTlIgTUVUIFRFTVAtR0VOIFNJREU |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | IPT EXH LWR INR MET TEMP-TURB SIDE | 3MT-TE011A | 1 | [8 empty] | 0-600 degC |  |  | Now: 320 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAyw0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklQVCBFWEggTFdSIElOUiBNRVQgVEVNUC1UVVJCIFNJREU |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | IPT EXH LWR INR MET TEMP-GEN SIDE | 3MT-TE011B | 1 | [8 empty] | 0-600 degC |  |  | Now: 320 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAyg0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklQVCBFWEggTFdSIElOUiBNRVQgVEVNUC1HRU4gU0lERQ |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | IPT EXH UPR INR MET TEMP-TURB SIDE | 3MT-TE012A | 1 | [8 empty] | 0-600 degC |  |  | Now: 320 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAzQ0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklQVCBFWEggVVBSIElOUiBNRVQgVEVNUC1UVVJCIFNJREU |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | IPT EXH UPR INR MET TEMP-GEN SIDE | 3MT-TE012B | 1 | [8 empty] | 0-600 degC |  |  | Now: 320 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAzA0AAAS1RKQi1LSTAwLVBJMVxUSkIzLklQVCBFWEggVVBSIElOUiBNRVQgVEVNUC1HRU4gU0lERQ |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | BRG 3 MET TEMP | 3MT-TE027 | 1 |  |  | -999999 |  |  | 0 |  | 115 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pANQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAzIE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | BRG 4 MET TEMP | 3MT-TE028 | 1 |  |  | -999999 |  |  | 0 |  | 115 | 0-150degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAOQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA0IE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | BRG 3 VIBN X | 3MT-VE003A | 1 | [7 empty] | 125 | 175 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pANwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAzIFZJQk4gWA |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | BRG 3 VIBN Y | 3MT-VE003B | 1 | [7 empty] | 125 | 175 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAOAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyAzIFZJQk4gWQ |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | BRG 4 VIBN X | 3MT-VE004A | 1 | [7 empty] | 125 | 175 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAOwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA0IFZJQk4gWA |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | BRG 4 VIBN Y | 3MT-VE004B | 1 | µmpp | [6 empty] | 125 | 175 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAPAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA0IFZJQk4gWQ |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | THRST BRG POSN A ABN | 3MT-ZE004A | 1 | mm |  | -0.51mm | -1.7mm |  |  |  | 1.47mm | 2.3mm |  |  | Now: -0.11mm |  | F1DPw1kUu10ziUaXEx2rIyo4pAvQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRIUlNUIEJSRyBQT1NOIEEgQUJO |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | THRST BRG POSN B ABN | 3MT-ZE004B | 1 | mm |  | -0.51mm | -1.7mm |  |  |  | 1.47mm | 2.3mm |  |  | Now: -0.11mm |  | F1DPw1kUu10ziUaXEx2rIyo4pAvg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRIUlNUIEJSRyBQT1NOIEIgQUJO |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | THRST BRG POSN C ABN | 3MT-ZE004C | 1 | mm |  | -0.51mm | -1.7mm |  |  |  | 1.47mm | 2.3mm |  |  | Now: -0.11mm |  | F1DPw1kUu10ziUaXEx2rIyo4pAvw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRIUlNUIEJSRyBQT1NOIEMgQUJO |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | THRST BRG FR/R MET TEMP | 3MT-TE023 | 1 |  |  | -999999 |  |  | 0 |  | 98 | 0-150degC | 0 |  | Now: 75.2 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAvA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRIUlNUIEJSRyBGUi9SIE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | THRST BRG FR/L MET TEMP | 3MT-TE024 | 1 |  |  | -999999 |  |  | 0 |  | 98 | 0-150degC | 0 |  | Now: 75.2 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAuw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRIUlNUIEJSRyBGUi9MIE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | THRST BRG RR/R MET TEMP | 3MT-TE025 | 1 |  |  | -999999 |  |  | 0 |  | 98 | 0-150degC | 0 |  | Now: 75.2 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAwg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRIUlNUIEJSRyBSUi9SIE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST020 | IP TURBINE | THRST BRG RR/L MET TEMP | 3MT-TE026 | 1 |  |  | -999999 |  |  | 0 |  | 98 | 0-150degC | 0 |  | Now: 75.2 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAwQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRIUlNUIEJSRyBSUi9MIE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST030A | LP TURBINE A | BRG 5 MET TEMP | 3MT-TE029 | 1 |  |  | -999999 |  |  | 0 |  | 107 | 0-150degC | 0 |  | Now: 85 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAPQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA1IE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST030A | LP TURBINE A | BRG 6 MET TEMP | 3MT-TE030 | 1 |  |  | -999999 |  |  | 0 |  | 107 | 0-150degC | 0 |  | Now: 85 degC |  | F1DPw1kUu10ziUaXEx2rIyo4pAQQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA2IE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST030A | LP TURBINE A | BRG 5 VIBN X | 3MT-VE005A | 1 | [5 empty] | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAPwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA1IFZJQk4gWA |  | 1
Turbine (TUR) | MT | 3MT-ST030A | LP TURBINE A | BRG 5 VIBN Y | 3MT-VE005B | 1 | µmpp |  |  |  |  | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAQAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA1IFZJQk4gWQ |  | 1
Turbine (TUR) | MT | 3MT-ST030A | LP TURBINE A | BRG 6 VIBN X | 3MT-VE006A | 1 | [5 empty] | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAQwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA2IFZJQk4gWA |  | 1
Turbine (TUR) | MT | 3MT-ST030A | LP TURBINE A | BRG 6 VIBN Y | 3MT-VE006B | 1 | [5 empty] | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pARAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA2IFZJQk4gWQ |  | 1
Turbine (TUR) | MT | 3MT-ST030A | LP TURBINE A | LPT EXHD TEMP A-TURB SIDE | 3MT-TE014A | 1 |  |  | -100000 |  |  |  |  | 80 | 107 |  |  | Now: 36.5 |  | F1DPw1kUu10ziUaXEx2rIyo4pAAA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBBIEVYSEQgVEVNUCBUVVJCIFNJREU |  | 1
| MT | 3MT-ST030B | LP TURBINE B | LPT B EXHD TEMP A-TURB SIDE | 3MT-TE014B | 1 |  |  | -100000 |  |  |  |  | 80 | 107 |  |  | Now: 36.5 |  | F1DPw1kUu10ziUaXEx2rIyo4pAAg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBCIEVYSEQgVEVNUCBUVVJCIFNJREU
Turbine (TUR) | MT | 3MT-ST030A | LP TURBINE A | LPT EXHD TEMP B-TURB SIDE | 3MT-TE015A | 1 |  |  | -100000 |  |  |  |  | 80 | 107 |  |  | Now: 36.5 |  | F1DPw1kUu10ziUaXEx2rIyo4pAAA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBBIEVYSEQgVEVNUCBUVVJCIFNJREU
Turbine (TUR) | MT | 3MT-ST030A | LP TURBINE A | LPT A EXHD TEMP TURB SIDE | 3MT-TE016A | 1 |  |  | -100000 |  |  |  |  | 80 | 107 |  |  | Now: 36.5 |  | F1DPw1kUu10ziUaXEx2rIyo4pAAA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBBIEVYSEQgVEVNUCBUVVJCIFNJREU
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT B EXHD TEMP TURB SIDE | 3MT-TE016B | 0 |  |  | -100000 |  |  |  |  | 80 | 107 |  |  | Now: 36.5 |  | F1DPw1kUu10ziUaXEx2rIyo4pAAg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBCIEVYSEQgVEVNUCBUVVJCIFNJREU
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | BRG 7 MET TEMP | 3MT-TE031 | 1 |  |  | -999999 |  |  | 0 |  | 107 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pARQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA3IE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | BRG 8 MET TEMP | 3MT-TE032 | 1 |  |  | -999999 |  |  | 0 |  | 107 |  | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pASQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA4IE1FVCBURU1Q |  | 1
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | BRG 7 VIBN X | 3MT-VE007A-N | 1 | µmpp |  |  |  |  | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pARwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA3IFZJQk4gWA |  | 1
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | BRG 7 VIBN Y | 3MT-VE007B-N | 1 | [5 empty] | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pASAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA3IFZJQk4gWQ |  | 1
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | BRG 8 VIBN X | 3MT-VE008A-N | 1 | [5 empty] | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pASwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA4IFZJQk4gWA |  | 1
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | BRG 8 VIBN Y | 3MT-VE008B-N | 1 | µmpp |  |  |  |  | 0 |  | 125 | 175 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pATAsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJSRyA4IFZJQk4gWQ |  | 1
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT LAST STG BDE TEMP | 3MT-TE013-H1 | 1 |  |  | -100000 |  |  | 0 |  | 220 | 280 | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAFQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBMQVNUIFNURyBCREUgVEVNUA
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT LAST STG BDE TEMP A | 3MT-TE013A | 1 | [7 empty] | 220 | 280 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAFg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBMQVNUIFNURyBCREUgVEVNUCBB
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT LAST STG BDE TEMP B | 3MT-TE013B | 1 | [7 empty] | 220 | 280 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAFw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBMQVNUIFNURyBCREUgVEVNUCBC
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT LAST STG BDE TEMP C | 3MT-TE013C | 1 | [7 empty] | 220 | 280 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAGA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBMQVNUIFNURyBCREUgVEVNUCBD
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT EXHD TEMP A-GEN SIDE | 3MT-TE017A | 1 | [7 empty] | 80 | 107 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAAQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBCIEVYSEQgVEVNUCBHRU4gU0lERQ |  | 1
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT B EXHD TEMP A-GEN SIDE | 3MT-TE017B | 1 | [7 empty] | 80 | 107 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAAQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBCIEVYSEQgVEVNUCBHRU4gU0lERQ
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT B EXHD TEMP GEN SIDE | 3MT-TE018A | 1 | [7 empty] | 80 | 107 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAAQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBCIEVYSEQgVEVNUCBHRU4gU0lERQ
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT A EXHD TEMP GEN SIDE | 3MT-TE019A | 1 | [7 empty] | 80 | 107 |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pA_w0AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBBIEVYSEQgVEVNUCBHRU4gU0lERQ
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | TURB ECC | 3MT-ZE001 | 1 |  |  | -999999 |  |  |  |  | 50 | 0-500umpp |  |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAxg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRVUkIgRUND |  | 1
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT DIFF EXP | 3MT-ZE005 | 1 | mm |  | 2025-07-02 |  |  | 0 |  | 47.3 | 0-50mm | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAFA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBESUZGIEVYUA |  | 1
FGD Support (SUP) | OA | 00OA-F851A | OXIDATION AIR BLOWER A
FGD Support (SUP) | OA | 00OA-F851B | OXIDATION AIR BLOWER B
FGD Support (SUP) | OA | 00OA-F851C | OXIDATION AIR BLOWER C
FGD Support (SUP) | OA | 00OA-M851A | OXIDATION AIR BLOWER A MOTOR | OXI AIR BLWR A CUR | 00OA-F851A-A | [14 empty] | 0
FGD Support (SUP) | OA | 00OA-M851A | OXIDATION AIR BLOWER A MOTOR | OXI AIR BLWR A MTR BRG NO.1 TEMP | 00OA-TE851 |  |  |  | -999999 | -999999 |  | 0 | 0 | 85 | 95 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851A | OXIDATION AIR BLOWER A MOTOR | OXI AIR BLWR A MTR BRG NO.2 TEMP | 00OA-TE852 |  |  |  | -999999 | -999999 |  | 0 | 0 | 85 | 95 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851A | OXIDATION AIR BLOWER A MOTOR | OXI AIR BLWR A MTR STAT WDG TEMP U | 00OA-TE853A |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851A | OXIDATION AIR BLOWER A MOTOR | OXI AIR BLWR A MTR STAT WDG TEMP U | 00OA-TE853B |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851A | OXIDATION AIR BLOWER A MOTOR | OXI AIR BLWR A MTR STAT WDG TEMP V | 00OA-TE854A |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851A | OXIDATION AIR BLOWER A MOTOR | OXI AIR BLWR A MTR STAT WDG TEMP V | 00OA-TE854B |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851A | OXIDATION AIR BLOWER A MOTOR | OXI AIR BLWR A MTR STAT WDG TEMP W | 00OA-TE855A |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851A | OXIDATION AIR BLOWER A MOTOR | OXI AIR BLWR A MTR STAT WDG TEMP W | 00OA-TE855B |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851B | OXIDATION AIR BLOWER B MOTOR | MTR CURRENT | 00OA-F851B-A | [14 empty] | 0
FGD Support (SUP) | OA | 00OA-M851B | OXIDATION AIR BLOWER B MOTOR | OXI AIR BLWR B MTR BRG NO.1 TEMP | 00OA-TE861 |  |  |  | -999999 | -999999 |  | 0 | 0 | 85 | 95 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851B | OXIDATION AIR BLOWER B MOTOR | OXI AIR BLWR B MTR BRG NO.2 TEMP | 00OA-TE862 |  |  |  | -999999 | -999999 |  | 0 | 0 | 85 | 95 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851B | OXIDATION AIR BLOWER B MOTOR | OXI AIR BLWR B MTR STAT WDG TEMP U | 00OA-TE863A |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851B | OXIDATION AIR BLOWER B MOTOR | OXI AIR BLWR B MTR STAT WDG TEMP U | 00OA-TE863B |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851B | OXIDATION AIR BLOWER B MOTOR | OXI AIR BLWR B MTR STAT WDG TEMP V | 00OA-TE864A |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851B | OXIDATION AIR BLOWER B MOTOR | OXI AIR BLWR B MTR STAT WDG TEMP V | 00OA-TE864B |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851B | OXIDATION AIR BLOWER B MOTOR | OXI AIR BLWR B MTR STAT WDG TEMP W | 00OA-TE865A |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851B | OXIDATION AIR BLOWER B MOTOR | OXI AIR BLWR B MTR STAT WDG TEMP W | 00OA-TE865B |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851C | OXIDATION AIR BLOWER C MOTOR | MTR CURRENT | 00OA-F851C-A | [14 empty] | 0
FGD Support (SUP) | OA | 00OA-M851C | OXIDATION AIR BLOWER C MOTOR | OXI AIR BLWR C MTR BRG NO.1 TEMP | 00OA-TE871 |  |  |  | -999999 | -999999 |  | 0 | 0 | 85 | 95 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851C | OXIDATION AIR BLOWER C MOTOR | OXI AIR BLWR C MTR BRG NO.2 TEMP | 00OA-TE872 |  |  |  | -999999 | -999999 |  | 0 | 0 | 85 | 95 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851C | OXIDATION AIR BLOWER C MOTOR | OXI AIR BLWR C MTR STAT WDG TEMP U | 00OA-TE873A |  |  |  | -999999 | -999999 |  | 0 | 0 | 85 | 95 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851C | OXIDATION AIR BLOWER C MOTOR | OXI AIR BLWR C MTR STAT WDG TEMP U | 00OA-TE873B |  |  |  | -999999 | -999999 |  | 0 | 0 | 85 | 95 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851C | OXIDATION AIR BLOWER C MOTOR | OXI AIR BLWR C MTR STAT WDG TEMP V | 00OA-TE874A |  |  |  | -999999 | -999999 |  | 0 | 0 | 85 | 95 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851C | OXIDATION AIR BLOWER C MOTOR | OXI AIR BLWR C MTR STAT WDG TEMP V | 00OA-TE874B |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851C | OXIDATION AIR BLOWER C MOTOR | OXI AIR BLWR C MTR STAT WDG TEMP W | 00OA-TE875A |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
FGD Support (SUP) | OA | 00OA-M851C | OXIDATION AIR BLOWER C MOTOR | OXI AIR BLWR C MTR STAT WDG TEMP W | 00OA-TE875B |  |  |  | -999999 | -999999 |  | 0 | 0 | 95 | 120 | 0 | 0 |  |  | 0
Chlorination (CP) | RO | 00RO-M101A | FLOW DIVISION CHAMBER WEIR PENSTOCK A MOTOR
Chlorination (CP) | RO | 00RO-M101B | FLOW DIVISION CHAMBER WEIR PENSTOCK B MOTOR
Chlorination (CP) | RO | 00RO-M101C | FLOW DIVISION CHAMBER WEIR PENSTOCK C MOTOR
Chlorination (CP) | RO | 00RO-M101D | FLOW DIVISION CHAMBER WEIR PENSTOCK D MOTOR
Chlorination (CP) | RO | 00RO-M110A | SEAWATER FEED PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M110B | SEAWATER FEED PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M110C | SEAWATER FEED PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M110D | SEAWATER FEED PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M120A | SEAWATER CLARIFIER SCRAPER A MOTOR
Chlorination (CP) | RO | 00RO-M120B | SEAWATER CLARIFIER SCRAPER B MOTOR
Chlorination (CP) | RO | 00RO-M120C | SEAWATER CLARIFIER SCRAPER C MOTOR
Chlorination (CP) | RO | 00RO-M120D | SEAWATER CLARIFIER SCRAPER D MOTOR
Chlorination (CP) | RO | 00RO-M122A | RO CLARIFLOCULATOR AGITATOR A MOTOR
Chlorination (CP) | RO | 00RO-M122B | RO CLARIFLOCULATOR AGITATOR B MOTOR
Chlorination (CP) | RO | 00RO-M122C | RO CLARIFLOCULATOR AGITATOR C MOTOR
Chlorination (CP) | RO | 00RO-M122D | RO CLARIFLOCULATOR AGITATOR D MOTOR
Chlorination (CP) | RO | 00RO-M126A | FILTER FEED PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M126B | FILTER FEED PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M126C | FILTER FEED PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M126D | FILTER FEED PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M130A | RO CLARIFIER SLUDGE PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M130B | RO CLARIFIER SLUDGE PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M130C | RO CLARIFIER SLUDGE PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M130D | RO CLARIFIER SLUDGE PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M140A | DIRTY WASH WATER PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M140B | DIRTY WASH WATER PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M150A | BACKWASH WATER PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M150B | BACKWASH WATER PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M152A | FILTER AIR BLOWER A MOTOR
Chlorination (CP) | RO | 00RO-M152B | FILTER AIR BLOWER B MOTOR
Chlorination (CP) | RO | 00RO-M160A | RO FEED BOOSTER PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M160B | RO FEED BOOSTER PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M160C | RO FEED BOOSTER PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M160D | RO FEED BOOSTER PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M161A | RO BLOWER ENCLOSURE FAN A MOTOR
Chlorination (CP) | RO | 00RO-M161B | RO BLOWER ENCLOSURE FAN B MOTOR
Chlorination (CP) | RO | 00RO-M170A | RO HIGH PRESSURE PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M170B | RO HIGH PRESSURE PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M170C | RO HIGH PRESSURE PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M170D | RO HIGH PRESSURE PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M180A | RO CLEANING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M180B | RO CLEANING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M181 | RO CLEANING TANK AGITATOR MOTOR
Chlorination (CP) | RO | 00RO-M190A | RO FLUSHING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M190B | RO FLUSHING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M195A | BRINE WATER PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M195B | BRINE WATER PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M210 | RO WASTEWATER CLARIFIER SCRAPPER MOTOR
Chlorination (CP) | RO | 00RO-M212A | RO WASTEWATER CLARIFIER SLUDGE PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M212B | RO WASTEWATER CLARIFIER SLUDGE PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M220A | RO THICKENER SLUDGE PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M220B | RO THICKENER SLUDGE PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M226A | RO ANIONIC POLYMER TANK AGITATOR A MOTOR
Chlorination (CP) | RO | 00RO-M226B | RO ANIONIC POLYMER TANK AGITATOR B MOTOR
Chlorination (CP) | RO | 00RO-M226C | RO ANIONIC POLYMER TANK AGITATOR C MOTOR
Chlorination (CP) | RO | 00RO-M228 | RO THICKENER SCRAPPER MOTOR
Chlorination (CP) | RO | 00RO-M230A | CLEAR WATER TRANSFER PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M230B | CLEAR WATER TRANSFER PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M231 | RO ANIONIC POLYMER FEED SCREW MOTOR
Chlorination (CP) | RO | 00RO-M234A | RO FeCl3 DOSING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M234B | RO FeCl3 DOSING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M234C | RO FeCl3 DOSING PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M234D | RO FeCl3 DOSING PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M240 | RO SBS TANK AGITATOR MOTOR
Chlorination (CP) | RO | 00RO-M241A | RO SLUDGE FeCl3 DOSING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M241B | RO SLUDGE FeCl3 DOSING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M242A | RO FeCl3 UNLOADING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M242B | RO FeCl3 UNLOADING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M250A | RO BIOCIDE NaOCl DOSING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M250B | RO BIOCIDE NaOCl DOSING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M250C | RO BIOCIDE NaOCl DOSING PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M250D | RO BIOCIDE NaOCl DOSING PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M251A | RO BIOCIDE NaOCl UNLOADING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M251B | RO BIOCIDE NaOCl UNLOADING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M252A | RO SLUDGE DEWATERING UNIT A MOTOR 1
Chlorination (CP) | RO | 00RO-M252B | RO SLUDGE DEWATERING UNIT B MOTOR 1
Chlorination (CP) | RO | 00RO-M253A | RO SLUDGE DEWATERING UNIT A MOTOR 2
Chlorination (CP) | RO | 00RO-M253B | RO SLUDGE DEWATERING UNIT B MOTOR 2
Chlorination (CP) | RO | 00RO-M255A | RO ANIONIC POLYMER DOSING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M255B | RO ANIONIC POLYMER DOSING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M255C | RO ANIONIC POLYMER DOSING PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M255D | RO ANIONIC POLYMER DOSING PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M260 | RO HOPPER MOTOR
Chlorination (CP) | RO | 00RO-M261A | RO SLUDGE ANIONIC POLYMER DOSING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M261B | RO SLUDGE ANIONIC POLYMER DOSING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M270A | RO SBS DOSING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M270B | RO SBS DOSING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M270C | RO SBS DOSING PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M270D | RO SBS DOSING PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M271 | RO SBS UNLOADING DRUM PUMP MOTOR
Chlorination (CP) | RO | 00RO-M272A | RO SBS SHOCK DOSING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M272B | RO SBS SHOCK DOSING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M274A | RO H2SO4 DOSING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M274B | RO H2SO4 DOSING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M274C | RO H2SO4 DOSING PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M274D | RO H2SO4 DOSING PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M280A | RO CATIONIC POLYMER TANK AGITATOR A MOTOR
Chlorination (CP) | RO | 00RO-M280B | RO CATIONIC POLYMER TANK AGITATOR B MOTOR
Chlorination (CP) | RO | 00RO-M280C | RO CATIONIC POLYMER TANK AGITATOR C MOTOR
Chlorination (CP) | RO | 00RO-M281A | RO H2SO4 UNLOADING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M281B | RO H2SO4 UNLOADING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M282 | RO CATIONIC POLYMER FEED SCREW MOTOR
Chlorination (CP) | RO | 00RO-M290A | RO ANTISCALANT DOSING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M290B | RO ANTISCALANT DOSING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M290C | RO ANTISCALANT DOSING PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M290D | RO ANTISCALANT DOSING PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M291 | RO ANTISCALANT UNLOADING DRUM PUMP MOTOR
Chlorination (CP) | RO | 00RO-M295 | RO CLEANING CHEMICAL UNLOADING DRUM PUMP Motor
Chlorination (CP) | RO | 00RO-M300A | RO NaOH DOSING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M300B | RO NaOH DOSING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M300C | RO NaOH DOSING PUMP C MOTOR
Chlorination (CP) | RO | 00RO-M300D | RO NaOH DOSING PUMP D MOTOR
Chlorination (CP) | RO | 00RO-M301A | RO NaOH UNLOADING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M301B | RO NaOH UNLOADING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M310A | RO CATIONIC POLYMER DOSING PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M310B | RO CATIONIC POLYMER DOSING PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M320A | RO CHEMICAL STORAGE YARD PIT PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M320B | RO CHEMICAL STORAGE YARD PIT PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M325 | RO ANTISCALANT TANK AGITATOR MOTOR
Chlorination (CP) | RO | 00RO-M330A | BRINE WATER PUMP PIT SUMP PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M330B | BRINE WATER PUMP PIT SUMP PUMP B MOTOR
Chlorination (CP) | RO | 00RO-M340A | RO CLEANING SUMP PUMP A MOTOR
Chlorination (CP) | RO | 00RO-M340B | RO CLEANING SUMP PUMP B MOTOR
Chlorination (CP) | RO | 00RO-P110A | SEAWATER FEED PUMP A
Chlorination (CP) | RO | 00RO-P110B | SEAWATER FEED PUMP B
Chlorination (CP) | RO | 00RO-P110C | SEAWATER FEED PUMP C
Chlorination (CP) | RO | 00RO-P110D | SEAWATER FEED PUMP D
Chlorination (CP) | RO | 00RO-P126A | FILTER FEED PUMP A
Chlorination (CP) | RO | 00RO-P126B | FILTER FEED PUMP B
Chlorination (CP) | RO | 00RO-P126C | FILTER FEED PUMP C
Chlorination (CP) | RO | 00RO-P126D | FILTER FEED PUMP D
Chlorination (CP) | RO | 00RO-P130A | RO CLARIFIER SLUDGE PUMP A
Chlorination (CP) | RO | 00RO-P130B | RO CLARIFIER SLUDGE PUMP B
Chlorination (CP) | RO | 00RO-P130C | RO CLARIFIER SLUDGE PUMP C
Chlorination (CP) | RO | 00RO-P130D | RO CLARIFIER SLUDGE PUMP D
Chlorination (CP) | RO | 00RO-P140A | DIRTY WASH WATER PUMP A
Chlorination (CP) | RO | 00RO-P140B | DIRTY WASH WATER PUMP B
Chlorination (CP) | RO | 00RO-P150A | BACKWASH WATER PUMP A
Chlorination (CP) | RO | 00RO-P150B | BACKWASH WATER PUMP B
Chlorination (CP) | RO | 00RO-P160A | RO FEED BOOSTER PUMP A
Chlorination (CP) | RO | 00RO-P160B | RO FEED BOOSTER PUMP B
Chlorination (CP) | RO | 00RO-P160C | RO FEED BOOSTER PUMP C
Chlorination (CP) | RO | 00RO-P160D | RO FEED BOOSTER PUMP D
Chlorination (CP) | RO | 00RO-P170A | RO HIGH PRESSURE PUMP A
Chlorination (CP) | RO | 00RO-P170B | RO HIGH PRESSURE PUMP B
Chlorination (CP) | RO | 00RO-P170C | RO HIGH PRESSURE PUMP C
Chlorination (CP) | RO | 00RO-P170D | RO HIGH PRESSURE PUMP D
Chlorination (CP) | RO | 00RO-P180A | RO CLEANING PUMP A
Chlorination (CP) | RO | 00RO-P180B | RO CLEANING PUMP B
Chlorination (CP) | RO | 00RO-P190A | RO FLUSHING PUMP A
Chlorination (CP) | RO | 00RO-P190B | RO FLUSHING PUMP B
Chlorination (CP) | RO | 00RO-P195A | BRINE WATER PUMP A
Chlorination (CP) | RO | 00RO-P195B | BRINE WATER PUMP B
Chlorination (CP) | RO | 00RO-P212A | RO WASTEWATER CLARIFIER SLUDGE PUMP A
Chlorination (CP) | RO | 00RO-P212B | RO WASTEWATER CLARIFIER SLUDGE PUMP B
Chlorination (CP) | RO | 00RO-P220A | RO THICKENER SLUDGE PUMP A
Chlorination (CP) | RO | 00RO-P220B | RO THICKENER SLUDGE PUMP B
Chlorination (CP) | RO | 00RO-P230A | CLEAR WATER TRANSFER PUMP A
Chlorination (CP) | RO | 00RO-P230B | CLEAR WATER TRANSFER PUMP B
Chlorination (CP) | RO | 00RO-P231 | RO ANIONIC POLYMER FEED SCREW
Chlorination (CP) | RO | 00RO-P234A | RO FeCl3 DOSING PUMP A
Chlorination (CP) | RO | 00RO-P234B | RO FeCl3 DOSING PUMP B
Chlorination (CP) | RO | 00RO-P234C | RO FeCl3 DOSING PUMP C
Chlorination (CP) | RO | 00RO-P234D | RO FeCl3 DOSING PUMP D
Chlorination (CP) | RO | 00RO-P241A | RO SLUDGE FeCl3 DOSING PUMP A
Chlorination (CP) | RO | 00RO-P241B | RO SLUDGE FeCl3 DOSING PUMP B
Chlorination (CP) | RO | 00RO-P242A | RO FeCl3 UNLOADING PUMP A
Chlorination (CP) | RO | 00RO-P242B | RO FeCl3 UNLOADING PUMP B
Chlorination (CP) | RO | 00RO-P250A | RO BIOCIDE NaOCl DOSING PUMP A
Chlorination (CP) | RO | 00RO-P250B | RO BIOCIDE NaOCl DOSING PUMP B
Chlorination (CP) | RO | 00RO-P250C | RO BIOCIDE NaOCl DOSING PUMP C
Chlorination (CP) | RO | 00RO-P250D | RO BIOCIDE NaOCl DOSING PUMP D
Chlorination (CP) | RO | 00RO-P251A | RO BIOCIDE NaOCl UNLOADING PUMP A
Chlorination (CP) | RO | 00RO-P251B | RO BIOCIDE NaOCl UNLOADING PUMP B
Chlorination (CP) | RO | 00RO-P255A | RO ANIONIC POLYMER DOSING PUMP A
Chlorination (CP) | RO | 00RO-P255B | RO ANIONIC POLYMER DOSING PUMP B
Chlorination (CP) | RO | 00RO-P255C | RO ANIONIC POLYMER DOSING PUMP C
Chlorination (CP) | RO | 00RO-P255D | RO ANIONIC POLYMER DOSING PUMP D
Chlorination (CP) | RO | 00RO-P261A | RO SLUDGE ANIONIC POLYMER DOSING PUMP A
Chlorination (CP) | RO | 00RO-P261B | RO SLUDGE ANIONIC POLYMER DOSING PUMP B
Chlorination (CP) | RO | 00RO-P270A | RO SBS DOSING PUMP A
Chlorination (CP) | RO | 00RO-P270B | RO SBS DOSING PUMP B
Chlorination (CP) | RO | 00RO-P270C | RO SBS DOSING PUMP C
Chlorination (CP) | RO | 00RO-P270D | RO SBS DOSING PUMP D
Chlorination (CP) | RO | 00RO-P271 | RO SBS UNLOADING DRUM PUMP
Chlorination (CP) | RO | 00RO-P272A | RO SBS SHOCK DOSING PUMP A
Chlorination (CP) | RO | 00RO-P272B | RO SBS SHOCK DOSING PUMP B
Chlorination (CP) | RO | 00RO-P274A | RO H2SO4 DOSING PUMP A | AUX STM DRN SEP OUTL TEMP A | 3AS-TE002A | 1 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pApgoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkFVWCBTVE0gRFJOIFNFUCBPVVRMIFRFTVAgQQ
Chlorination (CP) | RO | 00RO-P274B | RO H2SO4 DOSING PUMP B
Chlorination (CP) | RO | 00RO-P274C | RO H2SO4 DOSING PUMP C
Chlorination (CP) | RO | 00RO-P274D | RO H2SO4 DOSING PUMP D
Chlorination (CP) | RO | 00RO-P281A | RO H2SO4 UNLOADING PUMP A
Chlorination (CP) | RO | 00RO-P281B | RO H2SO4 UNLOADING PUMP B
Chlorination (CP) | RO | 00RO-P290A | RO ANTISCALANT DOSING PUMP A
Chlorination (CP) | RO | 00RO-P290B | RO ANTISCALANT DOSING PUMP B
Chlorination (CP) | RO | 00RO-P290C | RO ANTISCALANT DOSING PUMP C
Chlorination (CP) | RO | 00RO-P290D | RO ANTISCALANT DOSING PUMP D
Chlorination (CP) | RO | 00RO-P291 | RO ANTISCALANT UNLOADING DRUM PUMP
Chlorination (CP) | RO | 00RO-P295 | RO CLEANING CHEMICAL UNLOADING DRUM PUMP
Chlorination (CP) | RO | 00RO-P300A | RO NaOH DOSING PUMP A
Chlorination (CP) | RO | 00RO-P300B | RO NaOH DOSING PUMP B
Chlorination (CP) | RO | 00RO-P300C | RO NaOH DOSING PUMP C
Chlorination (CP) | RO | 00RO-P300D | RO NaOH DOSING PUMP D
Chlorination (CP) | RO | 00RO-P301A | RO NaOH UNLOADING PUMP A
Chlorination (CP) | RO | 00RO-P301B | RO NaOH UNLOADING PUMP B
Chlorination (CP) | RO | 00RO-P310A | RO CATIONIC POLYMER DOSING PUMP A
Chlorination (CP) | RO | 00RO-P310B | RO CATIONIC POLYMER DOSING PUMP B
Chlorination (CP) | RO | 00RO-P320A | RO CHEMICAL STORAGE YARD PIT PUMP A
Chlorination (CP) | RO | 00RO-P320B | RO CHEMICAL STORAGE YARD PIT PUMP B
Chlorination (CP) | RO | 00RO-P330A | BRINE WATER PUMP PIT SUMP PUMP A
Chlorination (CP) | RO | 00RO-P330B | BRINE WATER PUMP PIT SUMP PUMP B
Chlorination (CP) | RO | 00RO-P340A | RO CLEANING SUMP PUMP A
Chlorination (CP) | RO | 00RO-P340B | RO CLEANING SUMP PUMP B
Chlorination (CP) | RO | 00RO-Z110A | RO ENERGY RECOVERY TURBINE A
Chlorination (CP) | RO | 00RO-Z110B | RO ENERGY RECOVERY TURBINE B
Chlorination (CP) | RO | 00RO-Z110C | RO ENERGY RECOVERY TURBINE C
Chlorination (CP) | RO | 00RO-Z110D | RO ENERGY RECOVERY TURBINE D
FGD Support (SUP) | RP | 00RP-AG885 | MILL A OUTLET TANK AGITATOR
FGD Support (SUP) | RP | 00RP-AG925 | MILL B OUTLET TANK AGITATOR
FGD Support (SUP) | RP | 00RP-AG950 | LIMESTONE SLURRY STORAGE TANK AGITATOR | LMST SLRY STOR TK AG CUR | 00RP-AG950-A
FGD Support (SUP) | RP | 00RP-AG970 | LIMESTONE SLURRY FEED TANK AGITATOR
FGD Support (SUP) | RP | 00RP-AG985 | LIMESTONE PREP AREA SUMP AGITATOR
FGD Support (SUP) | RP | 00RP-BM871 | WET BALL MILL A
FGD Support (SUP) | RP | 00RP-BM911 | WET BALL MILL B
FGD Support (SUP) | RP | 00RP-CY871 | MILL A HYDROCLONE
FGD Support (SUP) | RP | 00RP-CY911 | MILL B HYDROCLONE
FGD Support (SUP) | RP | 00RP-DX837 | MILL B HDCLN OUTL SLRY DEN
FGD Support (SUP) | RP | 00RP-DX897 | MILL A HDCLN OUTL SLRY DEN
FGD Support (SUP) | RP | 00RP-DX979 | LMST SLRY FD TK PMP A/B OUTL DEN
FGD Support (SUP) | RP | 00RP-F991A | MILL A LOW PRESSURE LUBE OIL COOLING FAN A
FGD Support (SUP) | RP | 00RP-F991B | MILL A LOW PRESSURE LUBE OIL COOLING FAN B
FGD Support (SUP) | RP | 00RP-F995A | MILL B LOW PRESSURE LUBE OIL COOLING FAN A
FGD Support (SUP) | RP | 00RP-F995B | MILL BLOW PRESSURE LUBE OIL COOLING FAN B
FGD Support (SUP) | RP | 00RP-M856A | LIMESTONE WEIGHT FEEDER A MOTOR
FGD Support (SUP) | RP | 00RP-M856B | LIMESTONE WEIGHT FEEDER B MOTOR
FGD Support (SUP) | RP | 00RP-M871 | WET BALL MILL A INCHING DRIVE
FGD Support (SUP) | RP | 00RP-M871A | WET BALL MILL A MOTOR A | BALL MILL MN MTR BRG NO.1 TEMP | 00RP-TE871 |  |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0
FGD Support (SUP) | RP | 00RP-M871A | WET BALL MILL A MOTOR A | BALL MILL MN MTR BRG NO.2 TEMP | 00RP-TE872 |  |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0
FGD Support (SUP) | RP | 00RP-M871A | WET BALL MILL A MOTOR A | BALL MILL MN MTR STAT WDG TEMP U | 00RP-TE873A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAtgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBVMQ |  | 1
FGD Support (SUP) | RP | 00RP-M871A | WET BALL MILL A MOTOR A | BALL MILL MN MTR STAT WDG TEMP U | 00RP-TE873B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAtwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBVMg |  | 1
FGD Support (SUP) | RP | 00RP-M871A | WET BALL MILL A MOTOR A | BALL MILL MN MTR STAT WDG TEMP V | 00RP-TE874A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAuAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBWMQ |  | 1
FGD Support (SUP) | RP | 00RP-M871A | WET BALL MILL A MOTOR A | BALL MILL MN MTR STAT WDG TEMP V | 00RP-TE874B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAuQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBWMg |  | 1
FGD Support (SUP) | RP | 00RP-M871A | WET BALL MILL A MOTOR A | BALL MILL MN MTR STAT WDG TEMP W | 00RP-TE875A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAugwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBXMQ |  | 1
FGD Support (SUP) | RP | 00RP-M871A | WET BALL MILL A MOTOR A | BALL MILL MN MTR STAT WDG TEMP W | 00RP-TE875B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 105 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAuwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQSBNT1RPUiBXREcgVEVNUCBXMg |  | 1
FGD Support (SUP) | RP | 00RP-M871B | WET BALL MILL A MOTOR B | BALL MILL MN MTR BRG NO.1 TEMP | 00RP-TE911 |  |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0
FGD Support (SUP) | RP | 00RP-M871B | WET BALL MILL A MOTOR B | BALL MILL MN MTR BRG NO.2 TEMP | 00RP-TE912 |  |  |  | -999999 | -999999 |  | 0 | 0 | 90 | 100 | 0 | 0
FGD Support (SUP) | RP | 00RP-M871B | WET BALL MILL A MOTOR B | BALL MILL MN MTR STAT WDG TEMP U | 00RP-TE913A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAvQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBVMQ |  | 1
FGD Support (SUP) | RP | 00RP-M871B | WET BALL MILL A MOTOR B | BALL MILL MN MTR STAT WDG TEMP U | 00RP-TE913B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAvgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBVMg |  | 1
FGD Support (SUP) | RP | 00RP-M871B | WET BALL MILL A MOTOR B | BALL MILL MN MTR STAT WDG TEMP V | 00RP-TE914A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAvwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBWMQ |  | 1
FGD Support (SUP) | RP | 00RP-M871B | WET BALL MILL A MOTOR B | BALL MILL MN MTR STAT WDG TEMP V | 00RP-TE914B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAwAwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBWMg |  | 1
FGD Support (SUP) | RP | 00RP-M871B | WET BALL MILL A MOTOR B | BALL MILL MN MTR STAT WDG TEMP W | 00RP-TE915A | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAwQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBXMQ |  | 1
FGD Support (SUP) | RP | 00RP-M871B | WET BALL MILL A MOTOR B | BALL MILL MN MTR STAT WDG TEMP W | 00RP-TE915B | 1 |  |  | -999999 | -999999 |  | 0 | 0 | 130 | 135 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAwgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkZPUkNFRCBEUkFGVCBGQU4gQiBNT1RPUiBXREcgVEVNUCBXMg |  | 1
FGD Support (SUP) | RP | 00RP-M885 | MILL A OUTLET TANK AGITATOR MOTOR
FGD Support (SUP) | RP | 00RP-M891A | MILL A OUTLET TANK PUMP A MOTOR
FGD Support (SUP) | RP | 00RP-M891B | MILLA OUTLET TANK PUMP B MOTOR
FGD Support (SUP) | RP | 00RP-M911A | WET BALL MILL B MOTOR A | WET BALL MILL A MN DRV CUR | 00RP-M871A-A
FGD Support (SUP) | RP | 00RP-M911A | WET BALL MILL B MOTOR A | BALL MILL BRG NO.1 TEMP | 00RP-TE876 |  |  |  | -999999 | -999999 |  | 0 | 0 | 55 | 60 | 0 | 0
FGD Support (SUP) | RP | 00RP-M911A | WET BALL MILL B MOTOR A | BALL MILL BRG NO.2 TEMP | 00RP-TE877 |  |  |  | -999999 | -999999 |  | 0 | 0 | 55 | 60 | 0 | 0
FGD Support (SUP) | RP | 00RP-M911B | WET BALL MILL B MOTOR B | WET BALL MILL B MN DRV CUR | 00RP-M911A-A
FGD Support (SUP) | RP | 00RP-M911B | WET BALL MILL B MOTOR B | BALL MILL BRG NO.1 TEMP | 00RP-TE916 |  |  |  | -999999 | -999999 |  | 0 | 0 | 55 | 60 | 0 | 0
FGD Support (SUP) | RP | 00RP-M911B | WET BALL MILL B MOTOR B | BALL MILL BRG NO.2 TEMP | 00RP-TE917 |  |  |  | -999999 | -999999 |  | 0 | 0 | 55 | 60 | 0 | 0
FGD Support (SUP) | RP | 00RP-M925 | MILL B OUTLET TANK AGITATOR MOTOR
FGD Support (SUP) | RP | 00RP-M931A | MILL B OUTLET TANK PUMP A MOTOR
FGD Support (SUP) | RP | 00RP-M931B | MILL B OUTLET TANK PUMP B MOTOR
FGD Support (SUP) | RP | 00RP-M950 | LIMESTONE SLURRY STORAGE TANK AGITATOR MOTOR
FGD Support (SUP) | RP | 00RP-M952A | LIMESTONE SLURRY STORAGE TANK PUMP A MOTOR
FGD Support (SUP) | RP | 00RP-M952B | LIMESTONE SLURRY STORAGE TANK PUMP B MOTOR
FGD Support (SUP) | RP | 00RP-M970 | LIMESTONE SLURRY FEED TANK AGITATOR MOTOR
FGD Support (SUP) | RP | 00RP-M972A | LIMESTONE SLURRY FEED TANK PUMP A MOTOR
FGD Support (SUP) | RP | 00RP-M972B | LIMESTONE SLURRY FEED TANK PUMP B MOTOR
FGD Support (SUP) | RP | 00RP-M985 | LIMESTONE PREP AREA SUMP AGITATOR MOTOR
FGD Support (SUP) | RP | 00RP-M986A | LIMESTONE PREP AREA SUMP PUMP A MOTOR
FGD Support (SUP) | RP | 00RP-M986B | LIMESTONE PREP AREA SUMP PUMP B MOTOR
FGD Support (SUP) | RP | 00RP-P891A | MILL A OUTLET TANK PUMP A
FGD Support (SUP) | RP | 00RP-P891B | MILL A OUTLET TANK PUMP B
FGD Support (SUP) | RP | 00RP-P931A | MILL B OUTLET TANK PUMP A
FGD Support (SUP) | RP | 00RP-P931B | MILL B OUTLET TANK PUMP B
FGD Support (SUP) | RP | 00RP-P952A | LIMESTONE SLURRY STORAGE TANK PUMP A
FGD Support (SUP) | RP | 00RP-P952B | LIMESTONE SLURRY STORAGE TANK PUMP B
FGD Support (SUP) | RP | 00RP-P972A | LIMESTONE SLURRY FEED TANK PUMP A
FGD Support (SUP) | RP | 00RP-P972B | LIMESTONE SLURRY FEED TANK PUMP B
FGD Support (SUP) | RP | 00RP-P986A | LIMESTONE PREP AREA SUMP PUMP A
FGD Support (SUP) | RP | 00RP-P986B | LIMESTONE PREP AREA SUMP PUMP B
FGD Support (SUP) | RP | 00RP-P991A | MILL A LUBE OIL PUMP A
FGD Support (SUP) | RP | 00RP-P991B | MILL A LUBE OIL PUMP B
FGD Support (SUP) | RP | 00RP-P992 | MILL A GRSE PUMP
FGD Support (SUP) | RP | 00RP-P995 | MILL B GRSE PUMP
FGD Support (SUP) | RP | 00RP-P995A | MILL B LUBE OIL PUMP A
FGD Support (SUP) | RP | 00RP-P995B | MILL B LUBE OIL PUMP B
Screen & Filter (SCR) | SCR | NOT ELIGIBLE | Screening Plant (Intake)
Generator (GEN) | SCW | 3SCW-M001A | STATOR COOLING WATER PUMP MOTOR A
Generator (GEN) | SCW | 3SCW-M001B | STATOR COOLING WATER PUMP MOTOR B
Generator (GEN) | SCW | 3SCW-P001A | STATOR COOLING WATER PUMP A |  | NON DCS
Generator (GEN) | SCW | 3SCW-P001B | STATOR COOLING WATER PUMP B |  | NON DCS
Generator (GEN) | SO | 3SO-M001 | MAIN SEAL OIL PUMP MOTOR
Generator (GEN) | SO | 3SO-M002 | EMERGENCY SEAL OIL PUMP MOTOR
Generator (GEN) | SO | 3SO-P001 | MAIN SEAL OIL PUMP |  | NON DCS | [16 empty] | 666
Generator (GEN) | SO | 3SO-P002 | EMERGENCY SEAL OIL PUMP
Generator (GEN) | SSB | NOT ELIGIBLE | 500 kV Sub Station | [18 empty] | #REF!
Generator (GEN) | TR | 3TR-F301 | GT COOLING FAN MOTOR 1
Generator (GEN) | TR | 3TR-F302 | GT COOLING FAN MOTOR 2
Generator (GEN) | TR | 3TR-F303 | GT COOLING FAN MOTOR 3
Generator (GEN) | TR | 3TR-F304 | GT COOLING FAN MOTOR 4
Generator (GEN) | TR | 3TR-F305 | GT COOLING FAN MOTOR 5
Generator (GEN) | TR | 3TR-F306 | GT COOLING FAN MOTOR 6
Generator (GEN) | TR | 3TR-F307 | GT COOLING FAN MOTOR 7
Generator (GEN) | TR | 3TR-F308 | GT COOLING FAN MOTOR 8
Generator (GEN) | TR | 3TR-F309 | GT COOLING FAN MOTOR 9
Generator (GEN) | TR | 3TR-F310 | GT COOLING FAN MOTOR 10
Generator (GEN) | TR | 3TR-F311 | GT COOLING FAN MOTOR 11
Generator (GEN) | TR | 3TR-F312 | GT COOLING FAN MOTOR 12
Generator (GEN) | TR | 3TR-F313 | GT COOLING FAN MOTOR 13
Generator (GEN) | TR | 3TR-F314 | GT COOLING FAN MOTOR 14
[5 empty] | 1400 |  |  |  | 534 | 312 |  | 597 | 267 | 668 | 681 | 595 | 266

## Rep
SYSTEM | SUB-SYS | TAG LOCATION | EQUIPMENT | SENSOR | TAG SENSOR | Check | Unit | Threshold Status | S1L | S2L | S3L (Trip) | T1L | T2L | S1H (Alarm) | S2H (Fail) | T1H | T2H | NORMAL RANGE AT NEAR OR FULL LOAD | Check | Web_id | Id status
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(FREE SIDE) | 3AL-VE501A | 0 | µm |  | -999999 | -999999 |  | 0 | 0 | 75 um | 0-300um | 0 | 0 | now : 5,6um |  | F1DPw1kUu10ziUaXEx2rIyo4pAdw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBBIEJSRyBWSUIgTU9OSVRPUihGUkVFIFNJREUp | 1
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(MOTOR SIDE) | 3AL-VE502A | 0 |  |  | -999999 | -999999 |  | 0 | 0 | 75 um | 0-300um | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAeA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBBIEJSRyBWSUIgTU9OSVRPUihNT1RPUiBTSURFKQ | 1
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(FREE SIDE) | 3AL-VE501B | 0 | µm |  | -999999 | -999999 |  | 0 | 0 | 75 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBCIEJSRyBWSUIgTU9OSVRPUihGUkVFIFNJREUp | 1
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(MOTOR SIDE) | 3AL-VE502B | 0 |  |  | -999999 | -999999 |  | 0 | 0 | 75 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBCIEJSRyBWSUIgTU9OSVRPUihNT1RPUiBTSURFKQ | 1
Boiler (BOL) | BFT | 3BFT-AU040A | BFPT A TURNING GEAR | BFPT STM HDR PRESS | 3BFT-PIX001 | 0 | [8 empty] | 1-15barg |  |  | now:6.67barg |  | F1DPw1kUu10ziUaXEx2rIyo4pABwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgU1RNIEhEUiBQUkVTUw
Boiler (BOL) | BFT | 3BFT-AU040A | BFPT A TURNING GEAR | BFPT A SPD DMN FDBK | 3AEHC-CALC101 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA3AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBTUEQgRE1OIEZEQks
Boiler (BOL) | BFT | 3BFT-AU040A | BFPT A TURNING GEAR | BFPT A CNTL OIL PRESS | 3EHT-PIX001A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAzwoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBDTlRMIE9JTCBQUkVTUw
Boiler (BOL) | BFT | 3BFT-AU040A | BFPT A TURNING GEAR | BFPT A SSH PRESS | 3GST-PIX001A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA3QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBTU0ggUFJFU1M
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP | BFPT A LUB OIL FR DP | 3LOT-DPIX001A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA0woAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBMVUIgT0lMIEZSIERQ
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP | BFPT A LUB OIL PRESS | 3LOT-PIX001A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA1AoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQSBMVUIgT0lMIFBSRVNT
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP | BFPT B SPD DMN FDBK | 3BEHC-CALC101 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA-goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBTUEQgRE1OIEZEQks
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP | BFPT B CNTL OIL PRESS | 3EHT-PIX001B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA7QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBDTlRMIE9JTCBQUkVTUw
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP | BFPT B SSH PRESS | 3GST-PIX001B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA-woAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBTU0ggUFJFU1M
Feedwater (FW) | LOT | 3LOT-P080B | BFPT B OIL CONDITIONER FILTER PUMP | BFPT B LUB OIL FR DP | 3LOT-DPIX001B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA8QoAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBMVUIgT0lMIEZSIERQ
Feedwater (FW) | LOT | 3LOT-P080B | BFPT B OIL CONDITIONER FILTER PUMP | BFPT B LUB OIL PRESS | 3LOT-PIX001B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pA8goAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJGUFQgQiBMVUIgT0lMIFBSRVNT
Condensate Water (COND) | CO | 3CO-M001B | CONDENSATE EXTRACTION PUMP B MOTOR | CEP B MTR BRG 1 TEMP | 3CO-TE012B | 0 |  |  | -999999 |  |  | 0 |  | 100 | 0-200degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAsQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBCIE1UUiBCUkcgMSBURU1Q | 1
Boiler (BOL) | CW | 3CW-M020A | SEAWATER BOOSTER PUMP A MOTOR | SWBP A MTR WDG TEMP U | 3CW-TE013A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBNVFIgV0RHIFRFTVAgVQ
Boiler (BOL) | CW | 3CW-M020A | SEAWATER BOOSTER PUMP A MOTOR | SWBP A MTR WDG TEMP V | 3CW-TE015A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBNVFIgV0RHIFRFTVAgVg
Boiler (BOL) | CW | 3CW-M020A | SEAWATER BOOSTER PUMP A MOTOR | SWBP A MTR WDG TEMP W | 3CW-TE017A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBNVFIgV0RHIFRFTVAgVw
Boiler (BOL) | CW | 3CW-M020A | SEAWATER BOOSTER PUMP A MOTOR | SWBP A MTR BRG 1 TEMP | 3CW-TE019A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAew8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBNVFIgQlJHIDEgVEVNUA
Boiler (BOL) | CW | 3CW-M020A | SEAWATER BOOSTER PUMP A MOTOR | SWBP A MTR BRG 2 TEMP | 3CW-TE020A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAfA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBNVFIgQlJHIDIgVEVNUA
Boiler (BOL) | CW | 3CW-M020B | SEAWATER BOOSTER PUMP B MOTOR | SWBP B MTR WDG TEMP U | 3CW-TE013B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBNVFIgV0RHIFRFTVAgVQ
Boiler (BOL) | CW | 3CW-M020B | SEAWATER BOOSTER PUMP B MOTOR | SWBP B MTR WDG TEMP V | 3CW-TE015B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBNVFIgV0RHIFRFTVAgVg
Boiler (BOL) | CW | 3CW-M020B | SEAWATER BOOSTER PUMP B MOTOR | SWBP B MTR WDG TEMP W | 3CW-TE017B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAiA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBNVFIgV0RHIFRFTVAgVw
Boiler (BOL) | CW | 3CW-M020B | SEAWATER BOOSTER PUMP B MOTOR | SWBP B MTR BRG 1 TEMP | 3CW-TE019B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBNVFIgQlJHIDEgVEVNUA
Boiler (BOL) | CW | 3CW-M020B | SEAWATER BOOSTER PUMP B MOTOR | SWBP B MTR BRG 2 TEMP | 3CW-TE020B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAhA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBNVFIgQlJHIDIgVEVNUA
Boiler (BOL) | CW | 3CW-P011A | CIRCULATING WATER PUMP A MOTOR COOLING WATER BOOSTER PUMP | CWP A MTR CW FLW | 3CW-FIX001A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAMwwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBBIE1UUiBDVyBGTFc
Boiler (BOL) | CW | 3CW-P011B | CIRCULATING WATER PUMP B MOTOR COOLING WATER BOOSTER PUMP | CWP B MTR CW FLW | 3CW-FIX001B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAPgwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNXUCBCIE1UUiBDVyBGTFc
Boiler (BOL) | CW | 3CW-P020A | SEAWATER BOOSTER PUMP A | SWBP A DP | 3CW-DPIX002A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAeQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBEUA
Boiler (BOL) | CW | 3CW-P020A | SEAWATER BOOSTER PUMP A | SWBP A FLOW | 3PFC_OUT_TAG8 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAeg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQSBGTE9X
Boiler (BOL) | CW | 3CW-P020B | SEAWATER BOOSTER PUMP B | SWBP B DP | 3CW-DPIX002B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBEUA
Boiler (BOL) | CW | 3CW-P020B | SEAWATER BOOSTER PUMP B | SWBP B FLOW | 3PFC_OUT_TAG9 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAgg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlNXQlAgQiBGTE9X
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULVERIZER F MOTOR BEARING TEMP-DE | 3DP-TE737F | 0 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 0 | F1DPw1kUu10ziUaXEx2rIyo4pADg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBNT1RPUiBCRUFSSU5HIFRFTVAtREU | 1
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULVERIZER F MOTOR BEARING TEMP-NDE | 3DP-TE738F | 0 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 0 | F1DPw1kUu10ziUaXEx2rIyo4pADw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBNT1RPUiBCRUFSSU5HIFRFTVAtTkRF | 1
Boiler (BOL) | DP | 3DP-P761A | COAL PULVERIZER A LUBRICATING OIL PUMP | PULVERIZER-A LUB OIL TEMP. | 3DP-TE704A | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA0Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQSBMVUIgT0lMIFRFTVA | 1
Boiler (BOL) | DP | 3DP-P761B | COAL PULVERIZER B LUBRICATING OIL PUMP | PULVERIZER-B LUB OIL TEMP. | 3DP-TE704B | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA3Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQiBMVUIgT0lMIFRFTVA | 1
Boiler (BOL) | DP | 3DP-P761C | COAL PULVERIZER C LUBRICATING OIL PUMP | PULVERIZER-C LUB OIL TEMP. | 3DP-TE704C | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA6Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBMVUIgT0lMIFRFTVA | 1
Boiler (BOL) | DP | 3DP-P761D | COAL PULVERIZER D LUBRICATING OIL PUMP | PULVERIZER-D LUB OIL TEMP. | 3DP-TE704D | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA9Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRCBMVUIgT0lMIFRFTVA | 1
Boiler (BOL) | DP | 3DP-P761E | COAL PULVERIZER E LUBRICATING OIL PUMP | PULVERIZER-E LUB OIL TEMP. | 3DP-TE704E | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAAQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRSBMVUIgT0lMIFRFTVA | 1
Boiler (BOL) | DP | 3DP-P761F | COAL PULVERIZER F LUBRICATING OIL PUMP | PULVERIZER-F LUB OIL TEMP. | 3DP-TE704F | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pADQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBMVUIgT0lMIFRFTVA | 1
Boiler (BOL) | FO | 3FO-T509 | ACCUMULATOR | UNIT3 EDG FODTK INL FLOW | 3FO-FIX001 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjQwAAAS1RKQi1LSTAwLVBJMVxUSkIzLkVERyBGT0RUSyBJTkwgRkxX
Feedwater (FW) | FW | 3FW-M320 | MBFP MOTOR A | MBFP MTR A CUR | 3FW-P300-A1 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAPw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLk1CRlAgTVRSIEEgQ1VS
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A THRST BRG RTN OIL TEMP | 3LOT-TE006A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAnw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBUSFJTVCBCUkcgUlROIE9JTCBURU1Q
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A BP THRST BRG RTN OIL TEMP | 3LOT-TE007A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBCUCBUSFJTVCBCUkcgUlROIE9JTCBURU1Q
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A OUTL FLW | 3UCSA-CALC202 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAnA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBPVVRMIEZMVw
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A OUTL FLW CNTL DEVN | 3UCSA-CALC211 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAnQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBPVVRMIEZMVyBDTlRMIERFVk4
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A DIFF PRESS CNTL SV | 3UCSA-CALC212 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBESUZGIFBSRVNTIENOVEwgU1Y
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A DIFF PRESS | 3UCSA-CALC214 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAjw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBESUZGIFBSRVNT
Feedwater (FW) | LOT | 3LOT-T010A | BFPT A MAIN OIL TANK | TBFP A DIFF PRESS CNTL DEVN | 3UCSA-CALC215 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAkA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQSBESUZGIFBSRVNTIENOVEwgREVWTg
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B THRST BRG RTN OIL TEMP | 3LOT-TE006B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBUSFJTVCBCUkcgUlROIE9JTCBURU1Q
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B BP THRST BRG RTN OIL TEMP | 3LOT-TE007B | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAow8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBCUCBUSFJTVCBCUkcgUlROIE9JTCBURU1Q
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B OUTL FLW | 3UCSA-CALC203 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAsw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBPVVRMIEZMVw
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B OUTL FLW CNTL DEVN | 3UCSA-CALC216 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAtA8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBPVVRMIEZMVyBDTlRMIERFVk4
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B DIFF PRESS CNTL SV | 3UCSA-CALC217 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAqQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBESUZGIFBSRVNTIENOVEwgU1Y
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B DIFF PRESS | 3UCSA-CALC219 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pApg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBESUZGIFBSRVNT
Feedwater (FW) | LOT | 3LOT-T010A | BFPT B MAIN OIL TANK | TBFP B DIFF PRESS CNTL DEVN | 3UCSA-CALC220 | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pApw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlRCRlAgQiBESUZGIFBSRVNTIENOVEwgREVWTg
Air Flue Gas (AFG) | GG | 3GG-M853 | FGD BOOSTER FAN B MOTOR | CURRENT | 3GG-F852-A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAbwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgQ1VS | 1
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT B EXHD TEMP TURB SIDE | 3MT-TE016B | 0 |  |  | -100000 |  |  |  |  | 80 | 107 |  |  | Now: 36.5 |  | F1DPw1kUu10ziUaXEx2rIyo4pAAg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBCIEVYSEQgVEVNUCBUVVJCIFNJREU

## Reset
SYSTEM | SUB-SYS | TAG LOCATION | EQUIPMENT | SENSOR | TAG SENSOR | Check | Unit | Threshold Status | S1L | S2L | S3L (Trip) | T1L | T2L | S1H (Alarm) | S2H (Fail) | T1H | T2H | NORMAL RANGE AT NEAR OR FULL LOAD | Check | Web_id
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(FREE SIDE) | 3AL-VE501A | 0 | µm |  | -999999 | -999999 |  | 0 | 0 | 75 um | 0-300um | 0 | 0 | now : 5,6um |  | F1DPw1kUu10ziUaXEx2rIyo4pAdw4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBBIEJSRyBWSUIgTU9OSVRPUihGUkVFIFNJREUp
Air Flue Gas (AFG) | AL | 3AL-F501A | PRIMARY AIR FAN A | BRG VIB MONITOR(MOTOR SIDE) | 3AL-VE502A | 0 |  |  | -999999 | -999999 |  | 0 | 0 | 75 um | 0-300um | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAeA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBBIEJSRyBWSUIgTU9OSVRPUihNT1RPUiBTSURFKQ
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(FREE SIDE) | 3AL-VE501B | 0 | µm |  | -999999 | -999999 |  | 0 | 0 | 75 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfA4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBCIEJSRyBWSUIgTU9OSVRPUihGUkVFIFNJREUp
Air Flue Gas (AFG) | AL | 3AL-F501B | PRIMARY AIR FAN B | BRG VIB MONITOR(MOTOR SIDE) | 3AL-VE502B | 0 |  |  | -999999 | -999999 |  | 0 | 0 | 75 | 999999 | 0 | 0 |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAfQ4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBBRiBCIEJSRyBWSUIgTU9OSVRPUihNT1RPUiBTSURFKQ
Condensate Water (COND) | CO | 3CO-M001B | CONDENSATE EXTRACTION PUMP B MOTOR | CEP B MTR BRG 1 TEMP | 3CO-TE012B | 0 |  |  | -999999 |  |  | 0 |  | 100 | 0-200degC | 0 |  |  |  | F1DPw1kUu10ziUaXEx2rIyo4pAsQsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkNFUCBCIE1UUiBCUkcgMSBURU1Q
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULVERIZER F MOTOR BEARING TEMP-DE | 3DP-TE737F | 0 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 0 | F1DPw1kUu10ziUaXEx2rIyo4pADg8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBNT1RPUiBCRUFSSU5HIFRFTVAtREU
Boiler (BOL) | DP | 3DP-M731F | COAL PULVERIZER F MOTOR | PULVERIZER F MOTOR BEARING TEMP-NDE | 3DP-TE738F | 0 | [5 empty] | 0 | 0 | 95°C | 100°C (trip) | 0 | 0 | 60°C | 0 | F1DPw1kUu10ziUaXEx2rIyo4pADw8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBNT1RPUiBCRUFSSU5HIFRFTVAtTkRF
Boiler (BOL) | DP | 3DP-P761A | COAL PULVERIZER A LUBRICATING OIL PUMP | PULVERIZER-A LUB OIL TEMP. | 3DP-TE704A | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA0Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQSBMVUIgT0lMIFRFTVA
Boiler (BOL) | DP | 3DP-P761B | COAL PULVERIZER B LUBRICATING OIL PUMP | PULVERIZER-B LUB OIL TEMP. | 3DP-TE704B | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA3Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQiBMVUIgT0lMIFRFTVA
Boiler (BOL) | DP | 3DP-P761C | COAL PULVERIZER C LUBRICATING OIL PUMP | PULVERIZER-C LUB OIL TEMP. | 3DP-TE704C | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA6Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgQyBMVUIgT0lMIFRFTVA
Boiler (BOL) | DP | 3DP-P761D | COAL PULVERIZER D LUBRICATING OIL PUMP | PULVERIZER-D LUB OIL TEMP. | 3DP-TE704D | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pA9Q4AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRCBMVUIgT0lMIFRFTVA
Boiler (BOL) | DP | 3DP-P761E | COAL PULVERIZER E LUBRICATING OIL PUMP | PULVERIZER-E LUB OIL TEMP. | 3DP-TE704E | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pAAQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRSBMVUIgT0lMIFRFTVA
Boiler (BOL) | DP | 3DP-P761F | COAL PULVERIZER F LUBRICATING OIL PUMP | PULVERIZER-F LUB OIL TEMP. | 3DP-TE704F | 0 |  |  |  | 55°C |  | 0 |  | 60°C | 70°C (trip) | 0 |  | <55°C | 2 | F1DPw1kUu10ziUaXEx2rIyo4pADQ8AAAS1RKQi1LSTAwLVBJMVxUSkIzLlBVTFZFUklaRVIgRiBMVUIgT0lMIFRFTVA
Air Flue Gas (AFG) | GG | 3GG-M853 | FGD BOOSTER FAN B MOTOR | CURRENT | 3GG-F852-A | 0 | [13 empty] | F1DPw1kUu10ziUaXEx2rIyo4pAbwsAAAS1RKQi1LSTAwLVBJMVxUSkIzLkJTVFIgRkFOIEIgQ1VS
Turbine (TUR) | MT | 3MT-ST030B | LP TURBINE B | LPT B EXHD TEMP TURB SIDE | 3MT-TE016B | 0 |  |  | -100000 |  |  |  |  | 80 | 107 |  |  | Now: 36.5 |  | F1DPw1kUu10ziUaXEx2rIyo4pAAg4AAAS1RKQi1LSTAwLVBJMVxUSkIzLkxQVCBCIEVYSEQgVEVNUCBUVVJCIFNJREU

## NoSensor
SYSTEM | SUB-SYS | TAG LOCATION | EQUIPMENT | Y/T | SENSOR | S1L/S2L | T1L/T2L | S1H/S2H | T1H/T2H | TAG SENSOR | KODE XPS | ALM
Air Flue Gas (AFG) | AH | 3AH-AU501A | AH A SPEED REDUCER | T
Air Flue Gas (AFG) | AH | 3AH-AU501B | AH B SPEED REDUCER | T
Air Flue Gas (AFG) | AH | 3AH-H501A | REGENERATIVE AIR PREHEATER A | T
Air Flue Gas (AFG) | AH | 3AH-H501B | REGENERATIVE AIR PREHEATER B | T
Air Flue Gas (AFG) | AH | 3AH-M501A | REGENERATIVE AIR PREHEATER A MOTOR | T
Air Flue Gas (AFG) | AH | 3AH-M501B | REGENERATIVE AIR PREHEATER B MOTOR | T
Air Flue Gas (AFG) | AH | 3AH-M502A | RAPH A AIR MOTOR | T
Air Flue Gas (AFG) | AH | 3AH-M502B | RAPH B AIR MOTOR | T
Air Flue Gas (AFG) | AH | 3AH-M531A | RAPH A LUBRICATING OIL PUMP FOR HOT SIDE MOTOR | T
Air Flue Gas (AFG) | AH | 3AH-M531B | RAPH B LUBRICATING OIL PUMP FOR HOT SIDE MOTOR | T
Air Flue Gas (AFG) | AH | 3AH-P531A | RAPH A LUBRICATING OIL PUMP FOR HOT SIDE | T
Air Flue Gas (AFG) | AH | 3AH-P531B | RAPH B LUBRICATING OIL PUMP FOR HOT SIDE | T
Ash Handling (ASH) | BAD | 3BAD-M501 | DRAG CHAIN CONVEYOR MOTOR | Y | 3BAD-HSIG004 (current), SH1 = 10, SH2 = 11 A
Ash Handling (ASH) | BAD | 3BAD-M511A | DCC COOLING WATER RECIRCULATION PUMP A MOTOR | T
Ash Handling (ASH) | BAD | 3BAD-M511B | DCC COOLING WATER RECIRCULATION PUMP B MOTOR | T
|  | 3BAD-P511A | DCC COOLING WATER RECIRCULATION PUMP A | T
|  | 3BAD-P511B | DCC COOLING WATER RECIRCULATION PUMP B | T
Ash Handling (ASH) | BAD | 3BAD-M521A | DCC SLUDGE PUMP A MOTOR | T
Ash Handling (ASH) | BAD | 3BAD-M521B | DCC SLUDGE PUMP B MOTOR | T
Ash Handling (ASH) | BAD | 3BAD-P521A | DCC SLUDGE PUMP A | T
Ash Handling (ASH) | BAD | 3BAD-P521B | DCC SLUDGE PUMP B | T
Boiler (BOL) | BDW | 3BDW-M521A | BOILER WATER CIRCULATION PUMP A MOTOR | Y | CAVITY TEMP TE503A/B, SET TRIP LOKAL
Boiler (BOL) | BDW | 3BDW-M521A | BOILER WATER CIRCULATION PUMP A MOTOR | Y | CASING TEMP TE502A/B, SH1 = SET TRIP LOKAL? --> OM
Boiler (BOL) | BDW | 3BDW-M521A | BOILER WATER CIRCULATION PUMP A MOTOR | T | STAT WDG TEMP
Boiler (BOL) | BDW | 3BDW-M521B | BOILER WATER CIRCULATION PUMP B MOTOR | Y | CAVITY TEMP TE503A/B, SET TRIP LOKAL
Boiler (BOL) | BDW | 3BDW-M521B | BOILER WATER CIRCULATION PUMP B MOTOR | Y | CASING TEMP TE502A/B, SH1 = SET TRIP LOKAL? --> OM
Boiler (BOL) | BDW | 3BDW-M521B | BOILER WATER CIRCULATION PUMP B MOTOR | T | STAT WDG TEMP
Cooling Water (CW) | CCCW | 3CCCW-P090 | CCCW CHEMICAL DOSING PUMP | T
Coal Handling (CH) | CHA | 00CHA-CV801A | Motor Conveyor 101 A | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHA | 00CHA-CV802A | Motor Conveyor 102 A | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHA | 00CHA-CV803A | Motor Conveyor 103 A | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHA | 00CHA-CV801B | Motor Conveyor 101 B | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHA | 00CHA-CV802B | Motor Conveyor 102 B | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHA | 00CHA-CV803B | Motor Conveyor 103 B | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHA | 00CHA-CV804 | Motor Conveyor 104 | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHB | 00CHB-CV805A | Motor Conveyor 105 A | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHB | 00CHB-CV805B | Motor Conveyor 105 B | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHB | 00CHB-SKR805A | Bucket Wheel Motor of Stacker Reclaimer A | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHB | 00CHB-SKR805A | Boom Conveyor Motor of Stacker Reclaimer A | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHB | 00CHB-SKR805A | Slewing Motor of Stacker Reclaimer A | T
Coal Handling (CH) | CHB | 00CHB-SKR805A | Gantry Motor of Stacker Reclaimer A | T
Coal Handling (CH) | CHB | 00CHB-SKR805B | Bucket Wheel Motor of Stacker Reclaimer B | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHB | 00CHB-SKR805B | Boom Conveyor Motor of Stacker Reclaimer B | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Coal Handling (CH) | CHB | 00CHB-SKR805B | Slewing Motor of Stacker Reclaimer B | T
Coal Handling (CH) | CHB | 00CHB-SKR805B | Gantry Motor of Stacker Reclaimer B | T
Chlorination (CP) | CL | 00CL-M001A | CHLORINATION SYSTEM SEAWATER BOOSTER PUMP A MOTOR | T
Chlorination (CP) | CL | 00CL-M001B | CHLORINATION SYSTEM SEAWATER BOOSTER PUMP B MOTOR | T
Chlorination (CP) | CL | 00CL-P001A | CHLORINATION SYSTEM SEAWATER BOOSTER PUMP A | T
Chlorination (CP) | CL | 00CL-P001B | CHLORINATION SYSTEM SEAWATER BOOSTER PUMP B | T
Chlorination (CP) | CL | 00CL-M002A | CHLORINATION SYSTEM SODIUM HYPOCHLORITE DOSING PUMP A MOTOR | T
Chlorination (CP) | CL | 00CL-M002B | CHLORINATION SYSTEM SODIUM HYPOCHLORITE DOSING PUMP B MOTOR | T
Chlorination (CP) | CL | 00CL-M003 | CHLORINATION SYSTEM ACID PUMP MOTOR | T
Chlorination (CP) | CL | 00CL-M004A | CHLORINATION SYSTEM CHEMICAL SUMP PUMP A MOTOR | T
Chlorination (CP) | CL | 00CL-M004B | CHLORINATION SYSTEM CHEMICAL SUMP PUMP B MOTOR | T
Chlorination (CP) | CL | 00CL-M005A | CHLORINATION TRANSFORMER COOLING FAN 1A | T
Chlorination (CP) | CL | 00CL-M005B | CHLORINATION TRANSFORMER COOLING FAN 1B | T
Chlorination (CP) | CL | 00CL-M006A | CHLORINATION TRANSFORMER COOLING FAN 2A | T
Chlorination (CP) | CL | 00CL-M006B | CHLORINATION TRANSFORMER COOLING FAN 2B | T
Chlorination (CP) | CL | 00CL-M007A | CHLORINATION TRANSFORMER COOLING FAN 3A | T
Chlorination (CP) | CL | 00CL-M007B | CHLORINATION TRANSFORMER COOLING FAN 3B | T
Chlorination (CP) | CL | 00CL-M008A | CHLORINATION TRANSFORMER COOLING FAN 4A | T
Chlorination (CP) | CL | 00CL-M008B | CHLORINATION TRANSFORMER COOLING FAN 4B | T
Chlorination (CP) | CL | 00CL-M009A | CHLORINATION TRANSFORMER COOLING FAN 5A | T
Chlorination (CP) | CL | 00CL-M009B | CHLORINATION TRANSFORMER COOLING FAN 5B | T
Chlorination (CP) | CL | 00CL-Z002A | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR A2 | T
Chlorination (CP) | CL | 00CL-Z002B | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR B2 | T
Chlorination (CP) | CL | 00CL-Z002C | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR C2 | T
Chlorination (CP) | CL | 00CL-Z002D | CHLORINATION SYSTEM SODIUM HYPOCHLORITE GENERATOR D2 | T
Water Treatment Plant (WTP) | DMW | 00DMW-A385A | AIR DRYER A | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Water Treatment Plant (WTP) | DMW | 00DMW-A385B | AIR DRYER B | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Water Treatment Plant (WTP) | DMW | 00DMW-C375A | AIR COMPRESSOR A | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Water Treatment Plant (WTP) | DMW | 00DMW-C375B | AIR COMPRESSOR B | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Water Treatment Plant (WTP) | DMW | 00DMW-P375A | AIR COMPRESSOR A MOTOR | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Water Treatment Plant (WTP) | DMW | 00DMW-P375B | AIR COMPRESSOR B MOTOR | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Water Treatment Plant (WTP) | DMW | 00DMW-M110A | PRETREATED WATER PUMP A MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M110B | PRETREATED WATER PUMP B MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M190A | REGENERATION PUMP A MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M190B | REGENERATION PUMP B MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M200A | DMW NaOH UNLOADING PUMP A MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M200B | DMW NaOH UNLOADING PUMP B MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M220A | DMW NaOH TRANSFER PUMP A MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M220B | DMW NaOH TRANSFER PUMP B MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M300A | DMW HCl UNLOADING PUMP A MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M300B | DMW HCl UNLOADING PUMP B MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M320A | DMW HCl TRANSFER PUMP A MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M320B | DMW HCl TRANSFER PUMP B MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M360A | MIXED BED AIR BLOWER A MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M360B | MIXED BED AIR BLOWER B MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M370A | DMW NEUTRALIZATION PUMP A MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M370B | DMW NEUTRALIZATION PUMP B MOTOR | T
Water Treatment Plant (WTP) | DMW | 00DMW-M375A | AIR COMPRESSOR A MOTOR | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Water Treatment Plant (WTP) | DMW | 00DMW-M375B | AIR COMPRESSOR B MOTOR | Y | ADA SENSOR PLC, DIKUMPULKAN PERIODIK PER BULAN
Water Treatment Plant (WTP) | DMW | 00DMW-P100 | RESIN BACKWASH / TRANSFER PUMP | T
Boiler (BOL) | DP | 3DP-M712A | COAL FEEDER A CLEANOUT CONVEYOR MOTOR | T | AUXILIARRY
Boiler (BOL) | DP | 3DP-M712B | COAL FEEDER B CLEANOUT CONVEYOR MOTOR | T | AUXILIARRY
Boiler (BOL) | DP | 3DP-M712C | COAL FEEDER C CLEANOUT CONVEYOR MOTOR | T | AUXILIARRY
Boiler (BOL) | DP | 3DP-M712D | COAL FEEDER D CLEANOUT CONVEYOR MOTOR | T | AUXILIARRY
Boiler (BOL) | DP | 3DP-M712E | COAL FEEDER E CLEANOUT CONVEYOR MOTOR | T | AUXILIARRY
Boiler (BOL) | DP | 3DP-M712F | COAL FEEDER F CLEANOUT CONVEYOR MOTOR | T | AUXILIARRY
Boiler (BOL) | DP | 3DP-M741A | COAL PULVERIZER A ROTARY SEPARATOR MOTOR |  | 3DP-HSIG001 (CUR) --> PFD
Boiler (BOL) | DP | 3DP-M741B | COAL PULVERIZER B ROTARY SEPARATOR MOTOR |  | 3DP-HSIG003 (CUR)
Boiler (BOL) | DP | 3DP-M741C | COAL PULVERIZER C ROTARY SEPARATOR MOTOR |  | 3DP-HSIG005 (CUR)
Boiler (BOL) | DP | 3DP-M741D | COAL PULVERIZER D ROTARY SEPARATOR MOTOR |  | 3DP-HSIG007 (CUR)
Boiler (BOL) | DP | 3DP-M741E | COAL PULVERIZER E ROTARY SEPARATOR MOTOR |  | 3DP-HSIG009 (CUR)
Boiler (BOL) | DP | 3DP-M741F | COAL PULVERIZER F ROTARY SEPARATOR MOTOR |  | 3DP-HSIG0011 (CUR)
Boiler (BOL) | DP | 3DP-M761A | COAL PULVERIZER A LUBRICATING OIL PUMP MOTOR | T
Boiler (BOL) | DP | 3DP-M761B | COAL PULVERIZER B LUBRICATING OIL PUMP MOTOR | T
Boiler (BOL) | DP | 3DP-M761C | COAL PULVERIZER C LUBRICATING OIL PUMP MOTOR | T
Boiler (BOL) | DP | 3DP-M761D | COAL PULVERIZER D LUBRICATING OIL PUMP MOTOR | T
Boiler (BOL) | DP | 3DP-M761E | COAL PULVERIZER E LUBRICATING OIL PUMP MOTOR | T
Boiler (BOL) | DP | 3DP-M761F | COAL PULVERIZER F LUBRICATING OIL PUMP MOTOR | T
Boiler (BOL) | DP | 3DP-M781A | COAL PULVERIZER A HYDRAULIC OIL PUMP MOTOR | T
Boiler (BOL) | DP | 3DP-M781B | COAL PULVERIZER B HYDRAULIC OIL PUMP MOTOR | T
Boiler (BOL) | DP | 3DP-M781C | COAL PULVERIZER C HYDRAULIC OIL PUMP MOTOR | T
Boiler (BOL) | DP | 3DP-M781D | COAL PULVERIZER D HYDRAULIC OIL PUMP MOTOR | T
Boiler (BOL) | DP | 3DP-M781E | COAL PULVERIZER E HYDRAULIC OIL PUMP MOTOR | T
Boiler (BOL) | DP | 3DP-M781F | COAL PULVERIZER F HYDRAULIC OIL PUMP MOTOR | T
FGD Support (SUP) | DS | 00DS-M851 | GYPSUM HYDROCLONE OVERFLOW TANK AGITATOR MOTOR | T
FGD Support (SUP) | DS | 00DS-M860A | GYPSUM HYDROCLONE OVERFLOW TANK PUMP A MOTOR | T
FGD Support (SUP) | DS | 00DS-M860B | GYPSUM HYDROCLONE OVERFLOW TANK PUMP B MOTOR | T
FGD Support (SUP) | DS | 00DS-M883A | CHLORIDE PURGE TANK PUMP A MOTOR | T
FGD Support (SUP) | DS | 00DS-M883B | CHLORIDE PURGE TANK PUMP B MOTOR | T
FGD Support (SUP) | DS | 00DS-M888 | CHLORIDE PURGE TANK AGITATOR MOTOR | T
FGD Support (SUP) | DS | 00DS-M900 | VACUUM BELT FILTER A MOTOR | T
FGD Support (SUP) | DS | 00DS-M901 | VACUUM BELT FILTER A VACUUM PUMP MOTOR | Y | P901-A (CUR)
FGD Support (SUP) | DS | 00DS-P901 | VACUUM BELT FILTER A VACUUM PUMP | Y | P901-A (CUR)
FGD Support (SUP) | DS | 00DS-M902A | VACUUM BELT FILTER A WASH TANK PUMP A MOTOR | T
FGD Support (SUP) | DS | 00DS-M902B | VACUUM BELT FILTER A/ WASH TANK PUMP B MOTOR | T
FGD Support (SUP) | DS | 00DS-M935 | VACUUM BELT FILTER B MOTOR | T
FGD Support (SUP) | DS | 00DS-M936 | VACUUM BELT FILTER B VACUUM PUMP MOTOR | Y | P936-A (CUR)
FGD Support (SUP) | DS | 00DS-P936 | VACUUM BELT FILTER B VACUUM PUMP | Y | P936-A (CUR)
FGD Support (SUP) | DS | 00DS-M937A | VACUUM BELT FILTER B WASH TANK PUMP A MOTOR | T
FGD Support (SUP) | DS | 00DS-M937B | VACUUM BELT FILTER B WASH TANK PUMP B MOTOR | T
FGD Support (SUP) | DS | 00DS-M975 | RECLAIM WATER TANK AGITATOR MOTOR | T
FGD Support (SUP) | DS | 00DS-M978A | RECLAIM WATER TANK PUMP A MOTOR | T
FGD Support (SUP) | DS | 00DS-M978B | RECLAIM WATER TANK PUMP B MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD821 | ESP A CHAMBER 1 FIELD 1 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD822 | ESP A CHAMBER 2 FIELD 1 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD823 | ESP B CHAMBER 1 FIELD 1 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD824 | ESP B CHAMBER 2 FIELD 1 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD825 | ESP A CHAMBER 1 FIELD 2 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD826 | ESP A CHAMBER 2 FIELD 2 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD827 | ESP B CHAMBER 1 FIELD 2 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD828 | ESP B CHAMBER 2 FIELD 2 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD829 | ESP A CHAMBER 1 FIELD 3 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD830 | ESP A CHAMBER 2 FIELD 3 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD831 | ESP B CHAMBER 1 FIELD 3 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD832 | ESP B CHAMBER 2 FIELD 3 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD833 | ESP A CHAMBER 1 FIELD 4 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD834 | ESP A CHAMBER 2 FIELD 4 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD835 | ESP B CHAMBER 1 FIELD 4 - EMITTING RAPPING MOTOR | T
Air Flue Gas (AFG) | ESP | 3ESP-RD836 | ESP B CHAMBER 2 FIELD 4 - EMITTING RAPPING MOTOR | T
Boiler (BOL) | FO | 00FO-P802A | LFO FWD PMP A | Y | 00FO-PIX801 (BARG)
Boiler (BOL) | FO | 00FO-P802B | LFO FWD PMP B | Y | 00FO-PIX801 (BARG)
Generator (GEN) | GEN | 3GEN-M101A | THYRISTOR COOLING FAN MOTOR-A-1 | T | TIDAK TERIDENTIFIKASI, ON/OFF
Generator (GEN) | GEN | 3GEN-M101B | THYRISTOR COOLING FAN MOTOR-B-1 | T | TIDAK TERIDENTIFIKASI, ON/OFF
Generator (GEN) | GEN | 3GEN-M102A | THYRISTOR COOLING FAN MOTOR-A-2 | T | TIDAK TERIDENTIFIKASI, ON/OFF
Generator (GEN) | GEN | 3GEN-M102B | THYRISTOR COOLING FAN MOTOR-B-2 | T | TIDAK TERIDENTIFIKASI, ON/OFF
Generator (GEN) | GEN | 3GEN-M103A | THYRISTOR COOLING FAN MOTOR-A-3 | T | TIDAK TERIDENTIFIKASI, ON/OFF
Generator (GEN) | GEN | 3GEN-M103B | THYRISTOR COOLING FAN MOTOR-B-3 | T | TIDAK TERIDENTIFIKASI, ON/OFF
Generator (GEN) | GEN | 3GEN-M201A | GMCB COOLING FAN MOTOR-A | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M202A | GMCB COOLING FAN MOTOR-B | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M203A | GMCB COOLING FAN MOTOR-C | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M204A | GMCB COOLING FAN MOTOR-D | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M205A | GMCB COOLING FAN MOTOR-E | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M206A | GMCB COOLING FAN MOTOR-F | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M211A | GMCB RADIATOR COOLING FAN MOTOR-A1 | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M211B | GMCB RADIATOR COOLING FAN MOTOR-B1 | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M211C | GMCB RADIATOR COOLING FAN MOTOR-C1 | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M212A | GMCB RADIATOR COOLING FAN MOTOR-A2 | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M212B | GMCB RADIATOR COOLING FAN MOTOR-B2 | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M212C | GMCB RADIATOR COOLING FAN MOTOR-C2 | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M213A | GMCB RADIATOR COOLING FAN MOTOR-A3 | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M213B | GMCB RADIATOR COOLING FAN MOTOR-B3 | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M213C | GMCB RADIATOR COOLING FAN MOTOR-C3 | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M214A | GMCB RADIATOR COOLING FAN MOTOR-A4 | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M214B | GMCB RADIATOR COOLING FAN MOTOR-B4 | T | MCB TIDAK PERLU DIMONITOR
Generator (GEN) | GEN | 3GEN-M214C | GMCB RADIATOR COOLING FAN MOTOR-C4 | T | MCB TIDAK PERLU DIMONITOR
Air Flue Gas (AFG) | GG | 3GG-F802A | ID FAN A REGULATOR COOLING FAN A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F802B | ID FAN A REGULATOR COOLING FAN B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F803A | ID FAN A BEARING COOLING FAN A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F803B | ID FAN A BEARING COOLING FAN B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F804A | ID FAN B REGULATOR COOLING FAN A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F804B | ID FAN B REGULATOR COOLING FAN B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F805A | ID FAN B BEARING COOLING FAN A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F805B | ID FAN B BEARING COOLING FAN B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F851 | ULTRASONIC BIRD CONTROL | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F853A | FGD BOOSTER FAN A COOLING FAN MOTOR VERTICAL A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F853B | FGD BOOSTER FAN A COOLING FAN MOTOR VERTICAL B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F853C | FGD BOOSTER FAN A COOLING FAN MOTOR VERTICAL C | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F853D | FGD BOOSTER FAN A COOLING FAN MOTOR VERTICAL D | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F854A | FGD BOOSTER FAN B COOLING FAN MOTOR VERTICAL A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F854B | FGD BOOSTER FAN B COOLING FAN MOTOR VERTICAL B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F854C | FGD BOOSTER FAN B COOLING FAN MOTOR VERTICAL C | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F854D | FGD BOOSTER FAN B COOLING FAN MOTOR VERTICAL D | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F865A | HIGH PRESSURE SEAL AIR FAN A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F865B | HIGH PRESSURE SEAL AIR FAN B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F870A | LOW PRESSURE SEAL AIR FAN A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F870B | LOW PRESSURE SEAL AIR FAN B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F875A | FGD BOOSTER FAN A COOLING FAN A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F875B | FGD BOOSTER FAN A COOLING FAN B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F880A | FGD BOOSTER FAN B COOLING FAN A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-F880B | FGD BOOSTER FAN B COOLING FAN B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M865A | HIGH PRESSURE SEAL AIR FAN A MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M865B | HIGH PRESSURE SEAL AIR FAN B MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M870A | LOW PRESSURE SEAL AIR FAN A MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M870B | LOW PRESSURE SEAL AIR FAN B MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M875A | FGD BOOSTER FAN A COOLING FAN A MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M875B | FGD BOOSTER FAN A COOLING FAN B MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M877A | FGD BOOSTER FAN A LUBE OIL PUMP A MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M877B | FGD BOOSTER FAN A LUBE OIL PUMP B MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M878A | FGD BOOSTER FAN B LUBE OIL PUMP A MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M878B | FGD BOOSTER FAN B LUBE OIL PUMP B MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M880A | FGD BOOSTER FAN B COOLING FAN A MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-M880B | FGD BOOSTER FAN B COOLING FAN B MOTOR | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-P801A | ID FAN A OIL PUMP A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-P801B | ID FAN A OIL PUMP B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-P802A | ID FAN B OIL PUMP A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-P802B | ID FAN B OIL PUMP B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-P877A | FGD BOOSTER FAN A MOTOR LUBE OIL PUMP A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-P877B | FGD BOOSTER FAN A MOTOR LUBE OIL PUMP B | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-P878A | FGD BOOSTER FAN B MOTOR LUBE OIL PUMP A | T | ON/OFF
Air Flue Gas (AFG) | GG | 3GG-P878B | FGD BOOSTER FAN B MOTOR LUBE OIL PUMP B | T | ON/OFF
Turbine (TUR) | GSS | 3GSS-M011A | GLAND STEAM EXHAUSTER A MOTOR | T | ON/OFF
Turbine (TUR) | GSS | 3GSS-M011B | GLAND STEAM EXHAUSTER B MOTOR | T | ON/OFF
Feedwater (FW) | LOM | 3LOM-M330 | MBFP AUXILIARY OIL PUMP MOTOR | T
Feedwater (FW) | LOM | 3LOM-P330 | MBFP AUXILIARY OIL PUMP | T | ON/OFF
Feedwater (FW) | LOM | 3LOM-P370 | MBFP WORKING OIL PUMP | T | ON/OFF
Turbine (TUR) | LOS | 3LOS-M020A | MAIN OIL TANK VAPOUR EXTRACTOR A MOTOR | T | ON/OFF (ON SITE)
Turbine (TUR) | LOS | 3LOS-M020B | MAIN OIL TANK VAPOUR EXTRACTOR B MOTOR | T | ON/OFF (ON SITE)
Turbine (TUR) | LOS | 3LOS-M050 | EMERGENCY OIL PUMP MOTOR | T | ON/OFF (ON SITE)
Turbine (TUR) | LOS | 3LOS-M060 | MAIN OIL TANK TRANSFER PUMP MOTOR | T | ON/OFF (ON SITE)
Turbine (TUR) | LOS | 3LOS-M080 | MAIN OIL CONDITIONER FILTER PUMP MOTOR | T | ON/OFF (ON SITE)
Turbine (TUR) | LOS | 3LOS-P050 | EMERGENCY OIL PUMP | T | ON/OFF (ON SITE)
Turbine (TUR) | LOS | 3LOS-P060 | MAIN OIL TANK TRANSFER PUMP
Turbine (TUR) | LOS | 3LOS-P080 | MAIN OIL CONDITIONER FILTER PUMP
Feedwater (FW) | LOT | 3LOT-M050A | BFPT A EMERGENCY OIL PUMP MOTOR
Feedwater (FW) | LOT | 3LOT-M050B | BFPT B EMERGENCY OIL PUMP MOTOR
Feedwater (FW) | LOT | 3LOT-M080A | BFPT A OIL CONDITIONER FILTER PUMP MOTOR
Feedwater (FW) | LOT | 3LOT-M080B | BFPT B OIL CONDITIONER FILTER PUMP MOTOR
Feedwater (FW) | LOT | 3LOT-M120A | BFPT A MAIN OIL TANK VAPOUR EXTRACTOR MOTOR
Feedwater (FW) | LOT | 3LOT-M120B | BFPT B MAIN OIL TANK VAPOUR EXTRACTOR MOTOR
Feedwater (FW) | LOT | 3LOT-ME120 | BFPT OIL TANK OIL SEPARATOR
Feedwater (FW) | LOT | 3LOT-P050A | BFPT A EMERGENCY OIL PUMP
Feedwater (FW) | LOT | 3LOT-P050B | BFPT B EMERGENCY OIL PUMP
Feedwater (FW) | LOT | 3LOT-P080A | BFPT A OIL CONDITIONER FILTER PUMP
Feedwater (FW) | LOT | 3LOT-P080B | BFPT B OIL CONDITIONER FILTER PUMP
FGD Support (SUP) | LSH | 00LSH-F901 | CRSHR DUST COLLECTOR FAN | T
FGD Support (SUP) | LSH | 00LSH-F902 | LIMESTONE SILO DUST COLLECTOR FAN | T
FGD Support (SUP) | LSH | 00LSH-M852 | LIMESTONE BUCKET ELEVATOR MOTOR | T
FGD Support (SUP) | LSH | 00LSH-M901 | LIMESTONE CRUSHER DUST COLLECTOR FAN MOTOR | T
FGD Support (SUP) | OA | 00OA-F851A | OXIDATION AIR BLOWER A | T | IKUT MOTOR (CUR)
FGD Support (SUP) | OA | 00OA-F851B | OXIDATION AIR BLOWER B | T | IKUT MOTOR (CUR)
FGD Support (SUP) | OA | 00OA-F851C | OXIDATION AIR BLOWER C | T | IKUT MOTOR (CUR)
Chlorination (CP) | RO | 00RO-M101A | FLOW DIVISION CHAMBER WEIR PENSTOCK A MOTOR | T
Chlorination (CP) | RO | 00RO-M101B | FLOW DIVISION CHAMBER WEIR PENSTOCK B MOTOR | T
Chlorination (CP) | RO | 00RO-M101C | FLOW DIVISION CHAMBER WEIR PENSTOCK C MOTOR | T
Chlorination (CP) | RO | 00RO-M101D | FLOW DIVISION CHAMBER WEIR PENSTOCK D MOTOR | T
Chlorination (CP) | RO | 00RO-M120A | SEAWATER CLARIFIER SCRAPER A MOTOR | T
Chlorination (CP) | RO | 00RO-M120B | SEAWATER CLARIFIER SCRAPER B MOTOR | T
Chlorination (CP) | RO | 00RO-M120C | SEAWATER CLARIFIER SCRAPER C MOTOR | T
Chlorination (CP) | RO | 00RO-M120D | SEAWATER CLARIFIER SCRAPER D MOTOR | T
Chlorination (CP) | RO | 00RO-M122A | RO CLARIFLOCULATOR AGITATOR A MOTOR | T
Chlorination (CP) | RO | 00RO-M122B | RO CLARIFLOCULATOR AGITATOR B MOTOR | T
Chlorination (CP) | RO | 00RO-M122C | RO CLARIFLOCULATOR AGITATOR C MOTOR | T
Chlorination (CP) | RO | 00RO-M122D | RO CLARIFLOCULATOR AGITATOR D MOTOR | T
Chlorination (CP) | RO | 00RO-M126A | FILTER FEED PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M126B | FILTER FEED PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M126C | FILTER FEED PUMP C MOTOR | T
Chlorination (CP) | RO | 00RO-M126D | FILTER FEED PUMP D MOTOR | T
Chlorination (CP) | RO | 00RO-M130A | RO CLARIFIER SLUDGE PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M130B | RO CLARIFIER SLUDGE PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M130C | RO CLARIFIER SLUDGE PUMP C MOTOR | T
Chlorination (CP) | RO | 00RO-M130D | RO CLARIFIER SLUDGE PUMP D MOTOR | T
Chlorination (CP) | RO | 00RO-M140A | DIRTY WASH WATER PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M140B | DIRTY WASH WATER PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M150A | BACKWASH WATER PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M150B | BACKWASH WATER PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M152A | FILTER AIR BLOWER A MOTOR | T
Chlorination (CP) | RO | 00RO-M152B | FILTER AIR BLOWER B MOTOR | T
Chlorination (CP) | RO | 00RO-M160A | RO FEED BOOSTER PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M160B | RO FEED BOOSTER PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M160C | RO FEED BOOSTER PUMP C MOTOR | T
Chlorination (CP) | RO | 00RO-M160D | RO FEED BOOSTER PUMP D MOTOR | T
Chlorination (CP) | RO | 00RO-M161A | RO BLOWER ENCLOSURE FAN A MOTOR | T
Chlorination (CP) | RO | 00RO-M161B | RO BLOWER ENCLOSURE FAN B MOTOR | T
Chlorination (CP) | RO | 00RO-M170A | RO HIGH PRESSURE PUMP A MOTOR | Y | LOCAL CUR (PLC)
Chlorination (CP) | RO | 00RO-M170B | RO HIGH PRESSURE PUMP B MOTOR | Y | LOCAL CUR (PLC)
Chlorination (CP) | RO | 00RO-M170C | RO HIGH PRESSURE PUMP C MOTOR | Y | LOCAL CUR (PLC)
Chlorination (CP) | RO | 00RO-M170D | RO HIGH PRESSURE PUMP D MOTOR | Y | LOCAL CUR (PLC)
Chlorination (CP) | RO | 00RO-M180A | RO CLEANING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M180B | RO CLEANING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M181 | RO CLEANING TANK AGITATOR MOTOR | T
Chlorination (CP) | RO | 00RO-M190A | RO FLUSHING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M190B | RO FLUSHING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M195A | BRINE WATER PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M195B | BRINE WATER PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M210 | RO WASTEWATER CLARIFIER SCRAPPER MOTOR
Chlorination (CP) | RO | 00RO-M212A | RO WASTEWATER CLARIFIER SLUDGE PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M212B | RO WASTEWATER CLARIFIER SLUDGE PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M220A | RO THICKENER SLUDGE PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M220B | RO THICKENER SLUDGE PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M226A | RO ANIONIC POLYMER TANK AGITATOR A MOTOR | T
Chlorination (CP) | RO | 00RO-M226B | RO ANIONIC POLYMER TANK AGITATOR B MOTOR | T
Chlorination (CP) | RO | 00RO-M226C | RO ANIONIC POLYMER TANK AGITATOR C MOTOR | T
Chlorination (CP) | RO | 00RO-M228 | RO THICKENER SCRAPPER MOTOR
Chlorination (CP) | RO | 00RO-M230A | CLEAR WATER TRANSFER PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M230B | CLEAR WATER TRANSFER PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M231 | RO ANIONIC POLYMER FEED SCREW MOTOR
Chlorination (CP) | RO | 00RO-M234A | RO FeCl3 DOSING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M234B | RO FeCl3 DOSING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M234C | RO FeCl3 DOSING PUMP C MOTOR | T
Chlorination (CP) | RO | 00RO-M234D | RO FeCl3 DOSING PUMP D MOTOR | T
Chlorination (CP) | RO | 00RO-M240 | RO SBS TANK AGITATOR MOTOR | T
Chlorination (CP) | RO | 00RO-M241A | RO SLUDGE FeCl3 DOSING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M241B | RO SLUDGE FeCl3 DOSING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M242A | RO FeCl3 UNLOADING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M242B | RO FeCl3 UNLOADING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M250A | RO BIOCIDE NaOCl DOSING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M250B | RO BIOCIDE NaOCl DOSING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M250C | RO BIOCIDE NaOCl DOSING PUMP C MOTOR | T
Chlorination (CP) | RO | 00RO-M250D | RO BIOCIDE NaOCl DOSING PUMP D MOTOR | T
Chlorination (CP) | RO | 00RO-M251A | RO BIOCIDE NaOCl UNLOADING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M251B | RO BIOCIDE NaOCl UNLOADING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M252A | RO SLUDGE DEWATERING UNIT A MOTOR 1 | T
Chlorination (CP) | RO | 00RO-M252B | RO SLUDGE DEWATERING UNIT B MOTOR 1 | T
Chlorination (CP) | RO | 00RO-M253A | RO SLUDGE DEWATERING UNIT A MOTOR 2 | T
Chlorination (CP) | RO | 00RO-M253B | RO SLUDGE DEWATERING UNIT B MOTOR 2 | T
Chlorination (CP) | RO | 00RO-M255A | RO ANIONIC POLYMER DOSING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M255B | RO ANIONIC POLYMER DOSING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M255C | RO ANIONIC POLYMER DOSING PUMP C MOTOR | T
Chlorination (CP) | RO | 00RO-M255D | RO ANIONIC POLYMER DOSING PUMP D MOTOR | T
Chlorination (CP) | RO | 00RO-M260 | RO HOPPER MOTOR
Chlorination (CP) | RO | 00RO-M261A | RO SLUDGE ANIONIC POLYMER DOSING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M261B | RO SLUDGE ANIONIC POLYMER DOSING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M270A | RO SBS DOSING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M270B | RO SBS DOSING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M270C | RO SBS DOSING PUMP C MOTOR | T
Chlorination (CP) | RO | 00RO-M270D | RO SBS DOSING PUMP D MOTOR | T
Chlorination (CP) | RO | 00RO-M271 | RO SBS UNLOADING DRUM PUMP MOTOR | T
Chlorination (CP) | RO | 00RO-M272A | RO SBS SHOCK DOSING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M272B | RO SBS SHOCK DOSING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M274A | RO H2SO4 DOSING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M274B | RO H2SO4 DOSING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M274C | RO H2SO4 DOSING PUMP C MOTOR | T
Chlorination (CP) | RO | 00RO-M274D | RO H2SO4 DOSING PUMP D MOTOR | T
Chlorination (CP) | RO | 00RO-M280A | RO CATIONIC POLYMER TANK AGITATOR A MOTOR | T
Chlorination (CP) | RO | 00RO-M280B | RO CATIONIC POLYMER TANK AGITATOR B MOTOR | T
Chlorination (CP) | RO | 00RO-M280C | RO CATIONIC POLYMER TANK AGITATOR C MOTOR | T
Chlorination (CP) | RO | 00RO-M281A | RO H2SO4 UNLOADING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M281B | RO H2SO4 UNLOADING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M282 | RO CATIONIC POLYMER FEED SCREW MOTOR
Chlorination (CP) | RO | 00RO-M290A | RO ANTISCALANT DOSING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M290B | RO ANTISCALANT DOSING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M290C | RO ANTISCALANT DOSING PUMP C MOTOR | T
Chlorination (CP) | RO | 00RO-M290D | RO ANTISCALANT DOSING PUMP D MOTOR | T
Chlorination (CP) | RO | 00RO-M291 | RO ANTISCALANT UNLOADING DRUM PUMP MOTOR | T
Chlorination (CP) | RO | 00RO-M295 | RO CLEANING CHEMICAL UNLOADING DRUM PUMP Motor | T
Chlorination (CP) | RO | 00RO-M300A | RO NaOH DOSING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M300B | RO NaOH DOSING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M300C | RO NaOH DOSING PUMP C MOTOR | T
Chlorination (CP) | RO | 00RO-M300D | RO NaOH DOSING PUMP D MOTOR | T
Chlorination (CP) | RO | 00RO-M301A | RO NaOH UNLOADING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M301B | RO NaOH UNLOADING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M310A | RO CATIONIC POLYMER DOSING PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M310B | RO CATIONIC POLYMER DOSING PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M320A | RO CHEMICAL STORAGE YARD PIT PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M320B | RO CHEMICAL STORAGE YARD PIT PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M325 | RO ANTISCALANT TANK AGITATOR MOTOR | T
Chlorination (CP) | RO | 00RO-M330A | BRINE WATER PUMP PIT SUMP PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M330B | BRINE WATER PUMP PIT SUMP PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-M340A | RO CLEANING SUMP PUMP A MOTOR | T
Chlorination (CP) | RO | 00RO-M340B | RO CLEANING SUMP PUMP B MOTOR | T
Chlorination (CP) | RO | 00RO-P126A | FILTER FEED PUMP A
Chlorination (CP) | RO | 00RO-P126B | FILTER FEED PUMP B
Chlorination (CP) | RO | 00RO-P126C | FILTER FEED PUMP C
Chlorination (CP) | RO | 00RO-P126D | FILTER FEED PUMP D
Chlorination (CP) | RO | 00RO-P130A | RO CLARIFIER SLUDGE PUMP A
Chlorination (CP) | RO | 00RO-P130B | RO CLARIFIER SLUDGE PUMP B
Chlorination (CP) | RO | 00RO-P130C | RO CLARIFIER SLUDGE PUMP C
Chlorination (CP) | RO | 00RO-P130D | RO CLARIFIER SLUDGE PUMP D
Chlorination (CP) | RO | 00RO-P140A | DIRTY WASH WATER PUMP A
Chlorination (CP) | RO | 00RO-P140B | DIRTY WASH WATER PUMP B
Chlorination (CP) | RO | 00RO-P150A | BACKWASH WATER PUMP A
Chlorination (CP) | RO | 00RO-P150B | BACKWASH WATER PUMP B
Chlorination (CP) | RO | 00RO-P160A | RO FEED BOOSTER PUMP A
Chlorination (CP) | RO | 00RO-P160B | RO FEED BOOSTER PUMP B
Chlorination (CP) | RO | 00RO-P160C | RO FEED BOOSTER PUMP C
Chlorination (CP) | RO | 00RO-P160D | RO FEED BOOSTER PUMP D
Chlorination (CP) | RO | 00RO-P170A | RO HIGH PRESSURE PUMP A
Chlorination (CP) | RO | 00RO-P170B | RO HIGH PRESSURE PUMP B
Chlorination (CP) | RO | 00RO-P170C | RO HIGH PRESSURE PUMP C
Chlorination (CP) | RO | 00RO-P170D | RO HIGH PRESSURE PUMP D
Chlorination (CP) | RO | 00RO-P180A | RO CLEANING PUMP A
Chlorination (CP) | RO | 00RO-P180B | RO CLEANING PUMP B
Chlorination (CP) | RO | 00RO-P190A | RO FLUSHING PUMP A
Chlorination (CP) | RO | 00RO-P190B | RO FLUSHING PUMP B
Chlorination (CP) | RO | 00RO-P195A | BRINE WATER PUMP A | T
Chlorination (CP) | RO | 00RO-P195B | BRINE WATER PUMP B | T
Chlorination (CP) | RO | 00RO-P212A | RO WASTEWATER CLARIFIER SLUDGE PUMP A
Chlorination (CP) | RO | 00RO-P212B | RO WASTEWATER CLARIFIER SLUDGE PUMP B
Chlorination (CP) | RO | 00RO-P220A | RO THICKENER SLUDGE PUMP A
Chlorination (CP) | RO | 00RO-P220B | RO THICKENER SLUDGE PUMP B
Chlorination (CP) | RO | 00RO-P230A | CLEAR WATER TRANSFER PUMP A | T
Chlorination (CP) | RO | 00RO-P230B | CLEAR WATER TRANSFER PUMP B | T
Chlorination (CP) | RO | 00RO-P231 | RO ANIONIC POLYMER FEED SCREW
Chlorination (CP) | RO | 00RO-P234A | RO FeCl3 DOSING PUMP A | T
Chlorination (CP) | RO | 00RO-P234B | RO FeCl3 DOSING PUMP B | T
Chlorination (CP) | RO | 00RO-P234C | RO FeCl3 DOSING PUMP C | T
Chlorination (CP) | RO | 00RO-P234D | RO FeCl3 DOSING PUMP D | T
Chlorination (CP) | RO | 00RO-P241A | RO SLUDGE FeCl3 DOSING PUMP A | T
Chlorination (CP) | RO | 00RO-P241B | RO SLUDGE FeCl3 DOSING PUMP B | T
Chlorination (CP) | RO | 00RO-P242A | RO FeCl3 UNLOADING PUMP A | T
Chlorination (CP) | RO | 00RO-P242B | RO FeCl3 UNLOADING PUMP B | T
Chlorination (CP) | RO | 00RO-P250A | RO BIOCIDE NaOCl DOSING PUMP A | T
Chlorination (CP) | RO | 00RO-P250B | RO BIOCIDE NaOCl DOSING PUMP B | T
Chlorination (CP) | RO | 00RO-P250C | RO BIOCIDE NaOCl DOSING PUMP C | T
Chlorination (CP) | RO | 00RO-P250D | RO BIOCIDE NaOCl DOSING PUMP D | T
Chlorination (CP) | RO | 00RO-P251A | RO BIOCIDE NaOCl UNLOADING PUMP A | T
Chlorination (CP) | RO | 00RO-P251B | RO BIOCIDE NaOCl UNLOADING PUMP B | T
Chlorination (CP) | RO | 00RO-P255A | RO ANIONIC POLYMER DOSING PUMP A | T
Chlorination (CP) | RO | 00RO-P255B | RO ANIONIC POLYMER DOSING PUMP B | T
Chlorination (CP) | RO | 00RO-P255C | RO ANIONIC POLYMER DOSING PUMP C | T
Chlorination (CP) | RO | 00RO-P255D | RO ANIONIC POLYMER DOSING PUMP D | T
Chlorination (CP) | RO | 00RO-P261A | RO SLUDGE ANIONIC POLYMER DOSING PUMP A | T
Chlorination (CP) | RO | 00RO-P261B | RO SLUDGE ANIONIC POLYMER DOSING PUMP B | T
Chlorination (CP) | RO | 00RO-P270A | RO SBS DOSING PUMP A | T
Chlorination (CP) | RO | 00RO-P270B | RO SBS DOSING PUMP B | T
Chlorination (CP) | RO | 00RO-P270C | RO SBS DOSING PUMP C | T
Chlorination (CP) | RO | 00RO-P270D | RO SBS DOSING PUMP D | T
Chlorination (CP) | RO | 00RO-P271 | RO SBS UNLOADING DRUM PUMP | T
Chlorination (CP) | RO | 00RO-P272A | RO SBS SHOCK DOSING PUMP A | T
Chlorination (CP) | RO | 00RO-P272B | RO SBS SHOCK DOSING PUMP B | T
Chlorination (CP) | RO | 00RO-P274A | RO H2SO4 DOSING PUMP A | T
Chlorination (CP) | RO | 00RO-P274B | RO H2SO4 DOSING PUMP B | T
Chlorination (CP) | RO | 00RO-P274C | RO H2SO4 DOSING PUMP C | T
Chlorination (CP) | RO | 00RO-P274D | RO H2SO4 DOSING PUMP D | T
Chlorination (CP) | RO | 00RO-P281A | RO H2SO4 UNLOADING PUMP A | T
Chlorination (CP) | RO | 00RO-P281B | RO H2SO4 UNLOADING PUMP B | T
Chlorination (CP) | RO | 00RO-P290A | RO ANTISCALANT DOSING PUMP A | T
Chlorination (CP) | RO | 00RO-P290B | RO ANTISCALANT DOSING PUMP B | T
Chlorination (CP) | RO | 00RO-P290C | RO ANTISCALANT DOSING PUMP C | T
Chlorination (CP) | RO | 00RO-P290D | RO ANTISCALANT DOSING PUMP D | T
Chlorination (CP) | RO | 00RO-P291 | RO ANTISCALANT UNLOADING DRUM PUMP | T
Chlorination (CP) | RO | 00RO-P295 | RO CLEANING CHEMICAL UNLOADING DRUM PUMP | T
Chlorination (CP) | RO | 00RO-P300A | RO NaOH DOSING PUMP A | T
Chlorination (CP) | RO | 00RO-P300B | RO NaOH DOSING PUMP B | T
Chlorination (CP) | RO | 00RO-P300C | RO NaOH DOSING PUMP C | T
Chlorination (CP) | RO | 00RO-P300D | RO NaOH DOSING PUMP D | T
Chlorination (CP) | RO | 00RO-P301A | RO NaOH UNLOADING PUMP A | T
Chlorination (CP) | RO | 00RO-P301B | RO NaOH UNLOADING PUMP B | T
Chlorination (CP) | RO | 00RO-P310A | RO CATIONIC POLYMER DOSING PUMP A | T
Chlorination (CP) | RO | 00RO-P310B | RO CATIONIC POLYMER DOSING PUMP B | T
Chlorination (CP) | RO | 00RO-P320A | RO CHEMICAL STORAGE YARD PIT PUMP A | T
Chlorination (CP) | RO | 00RO-P320B | RO CHEMICAL STORAGE YARD PIT PUMP B | T
Chlorination (CP) | RO | 00RO-P330A | BRINE WATER PUMP PIT SUMP PUMP A | T
Chlorination (CP) | RO | 00RO-P330B | BRINE WATER PUMP PIT SUMP PUMP B | T
Chlorination (CP) | RO | 00RO-P340A | RO CLEANING SUMP PUMP A | T
Chlorination (CP) | RO | 00RO-P340B | RO CLEANING SUMP PUMP B | T
Chlorination (CP) | RO | 00RO-Z110A | RO ENERGY RECOVERY TURBINE A
Chlorination (CP) | RO | 00RO-Z110B | RO ENERGY RECOVERY TURBINE B
Chlorination (CP) | RO | 00RO-Z110C | RO ENERGY RECOVERY TURBINE C
Chlorination (CP) | RO | 00RO-Z110D | RO ENERGY RECOVERY TURBINE D
FGD Support (SUP) | RP | 00RP-AG885 | MILL A OUTLET TANK AGITATOR
FGD Support (SUP) | RP | 00RP-AG925 | MILL B OUTLET TANK AGITATOR
FGD Support (SUP) | RP | 00RP-AG970 | LIMESTONE SLURRY FEED TANK AGITATOR
FGD Support (SUP) | RP | 00RP-AG985 | LIMESTONE PREP AREA SUMP AGITATOR
FGD Support (SUP) | RP | 00RP-BM871 | WET BALL MILL A
FGD Support (SUP) | RP | 00RP-BM911 | WET BALL MILL B
FGD Support (SUP) | RP | 00RP-CY871 | MILL A HYDROCLONE
FGD Support (SUP) | RP | 00RP-CY911 | MILL B HYDROCLONE
FGD Support (SUP) | RP | 00RP-DX837 | MILL B HDCLN OUTL SLRY DEN
FGD Support (SUP) | RP | 00RP-DX897 | MILL A HDCLN OUTL SLRY DEN
FGD Support (SUP) | RP | 00RP-DX979 | LMST SLRY FD TK PMP A/B OUTL DEN
FGD Support (SUP) | RP | 00RP-F991A | MILL A LOW PRESSURE LUBE OIL COOLING FAN A
FGD Support (SUP) | RP | 00RP-F991B | MILL A LOW PRESSURE LUBE OIL COOLING FAN B
FGD Support (SUP) | RP | 00RP-F995A | MILL B LOW PRESSURE LUBE OIL COOLING FAN A
FGD Support (SUP) | RP | 00RP-F995B | MILL BLOW PRESSURE LUBE OIL COOLING FAN B
FGD Support (SUP) | RP | 00RP-M856A | LIMESTONE WEIGHT FEEDER A MOTOR
FGD Support (SUP) | RP | 00RP-M856B | LIMESTONE WEIGHT FEEDER B MOTOR
FGD Support (SUP) | RP | 00RP-M885 | MILL A OUTLET TANK AGITATOR MOTOR
FGD Support (SUP) | RP | 00RP-M891A | MILL A OUTLET TANK PUMP A MOTOR
FGD Support (SUP) | RP | 00RP-M891B | MILLA OUTLET TANK PUMP B MOTOR
FGD Support (SUP) | RP | 00RP-M925 | MILL B OUTLET TANK AGITATOR MOTOR
FGD Support (SUP) | RP | 00RP-M931A | MILL B OUTLET TANK PUMP A MOTOR
FGD Support (SUP) | RP | 00RP-M931B | MILL B OUTLET TANK PUMP B MOTOR
FGD Support (SUP) | RP | 00RP-M950 | LIMESTONE SLURRY STORAGE TANK AGITATOR MOTOR
FGD Support (SUP) | RP | 00RP-M952A | LIMESTONE SLURRY STORAGE TANK PUMP A MOTOR
FGD Support (SUP) | RP | 00RP-M952B | LIMESTONE SLURRY STORAGE TANK PUMP B MOTOR
FGD Support (SUP) | RP | 00RP-M970 | LIMESTONE SLURRY FEED TANK AGITATOR MOTOR
FGD Support (SUP) | RP | 00RP-M972A | LIMESTONE SLURRY FEED TANK PUMP A MOTOR
FGD Support (SUP) | RP | 00RP-M972B | LIMESTONE SLURRY FEED TANK PUMP B MOTOR
FGD Support (SUP) | RP | 00RP-M985 | LIMESTONE PREP AREA SUMP AGITATOR MOTOR
FGD Support (SUP) | RP | 00RP-M986A | LIMESTONE PREP AREA SUMP PUMP A MOTOR
FGD Support (SUP) | RP | 00RP-M986B | LIMESTONE PREP AREA SUMP PUMP B MOTOR
FGD Support (SUP) | RP | 00RP-P891A | MILL A OUTLET TANK PUMP A
FGD Support (SUP) | RP | 00RP-P891B | MILL A OUTLET TANK PUMP B
FGD Support (SUP) | RP | 00RP-P931A | MILL B OUTLET TANK PUMP A
FGD Support (SUP) | RP | 00RP-P931B | MILL B OUTLET TANK PUMP B
FGD Support (SUP) | RP | 00RP-P952A | LIMESTONE SLURRY STORAGE TANK PUMP A
FGD Support (SUP) | RP | 00RP-P952B | LIMESTONE SLURRY STORAGE TANK PUMP B
FGD Support (SUP) | RP | 00RP-P972A | LIMESTONE SLURRY FEED TANK PUMP A
FGD Support (SUP) | RP | 00RP-P972B | LIMESTONE SLURRY FEED TANK PUMP B
FGD Support (SUP) | RP | 00RP-P986A | LIMESTONE PREP AREA SUMP PUMP A
FGD Support (SUP) | RP | 00RP-P986B | LIMESTONE PREP AREA SUMP PUMP B
FGD Support (SUP) | RP | 00RP-P991A | MILL A LUBE OIL PUMP A
FGD Support (SUP) | RP | 00RP-P991B | MILL A LUBE OIL PUMP B
FGD Support (SUP) | RP | 00RP-P992 | MILL A GRSE PUMP
FGD Support (SUP) | RP | 00RP-P995 | MILL B GRSE PUMP
FGD Support (SUP) | RP | 00RP-P995A | MILL B LUBE OIL PUMP A
FGD Support (SUP) | RP | 00RP-P995B | MILL B LUBE OIL PUMP B
Generator (GEN) | SO | 3SO-M001 | MAIN SEAL OIL PUMP MOTOR
Generator (GEN) | SO | 3SO-M002 | EMERGENCY SEAL OIL PUMP MOTOR
Generator (GEN) | SO | 3SO-P002 | EMERGENCY SEAL OIL PUMP
Generator (GEN) | TR | 3TR-F301 | GT COOLING FAN MOTOR 1 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F302 | GT COOLING FAN MOTOR 2 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F303 | GT COOLING FAN MOTOR 3 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F304 | GT COOLING FAN MOTOR 4 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F305 | GT COOLING FAN MOTOR 5 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F306 | GT COOLING FAN MOTOR 6 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F307 | GT COOLING FAN MOTOR 7 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F308 | GT COOLING FAN MOTOR 8 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F309 | GT COOLING FAN MOTOR 9 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F310 | GT COOLING FAN MOTOR 10 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F311 | GT COOLING FAN MOTOR 11 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F312 | GT COOLING FAN MOTOR 12 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F313 | GT COOLING FAN MOTOR 13 | T | LOCAL WARNING (SWITCH)
Generator (GEN) | TR | 3TR-F314 | GT COOLING FAN MOTOR 14 | T | LOCAL WARNING (SWITCH)